## Main
[5 empty] | 2 | NC | CASBEE for Building Design (New Construction) 2024 Edition
Assessment Software | [5 empty] | NC | CASBEE for Building Design (New Construction) 2024 Edition
Version | CASBEE-BD_NCe_2024_v1.21 |  |  |  |  | EB | CASBEE-建築(既存)2016年版
n Assessment Manual : | CASBEE for Building Design (New Construction) 2024 Edition |  |  |  |  | TC | CASBEE-短期使用2016年版
[6 empty] | IS | CASBEE-ｲﾝﾃﾘｱｽﾍﾟｰｽ2016年版
1) Summary input
[1] Building outline
n Building Name | XXX Building |  |  |  | Zone 1 | 地域区分Ⅰ | 1
n Location / Region | XX City, XX Prefecture |  |  | Zone 3 | Zone 2 | 地域区分Ⅱ | 2
[5 empty] | Zone 3 | 地域区分Ⅲ | 3
n Area / Zone | Commercial zone |  |  |  | Zone 4 | 地域区分Ⅳ | 4
n Date of completion | 2027-03-01 | (Scheduled/Completed) |  | Scheduled | Zone 5 | 地域区分Ⅴ | 5
| 2016年６月～８月 |  |  |  | Zone 6 | 地域区分Ⅵ | 6
n Site Area | 5000 | ㎡ |  |  | Zone 7 |  | 7
n Construction Area | 4000 | ㎡ |  |  | Zone 8 |  | 8
n Gross Floor Area | 7000 | ㎡ |  |  |  |  | 3
n Building Type | XX |  |  |  | Scheduled
| Offices, |  |  |  | Completed
n Number of Floors | + XX F
n Structure | RC |  |  |  | S | RC | SRC | Wood
② 評価対象概要
■ 評価対象名称 | ○○サービス
■ 評価対象用途 | ○○
■ 使用開始 | 2014-07-11
■ 専用面積 | XXX | ㎡
■ 専用部の階 | 地上○○F～○○F
n Occupancy | XX | Occupants (assumed)
n Average Annual Occupancy | XXX | hrs./yr. (assumed) |  |  | 年間使用時間 | 日平均使用時間
■ 日平均使用時間 | XXX | 時間/日（想定値）
[5 empty] | EB | 0
[5 empty] | Preliminary design stage | 2
[2] Implementation of Assessment |  |  |  |  | Execution design stage | 2 |  | NC | 既存学校版
n Assessment date | 2025-07-08 |  | Execution design stage |  | Construction completion stage | 2 |  | Preliminary design stage | 簡易評価
n Assessor | XXXXX |  |  |  | 短期使用 | 3 |  | Execution design stage | 省エネルギー計画書による評価
n Date of confirmation | 2025-07-10 |  |  |  | インテリア | 4 |  | Construction completion stage
n Confirmed by | XXXXX
n WLC calculation | Std. Calc | --> Input WLC Calculation Conditions Sheet (Std. calc) |  |  | Std. Calc | Standard calculation |  | --> Input WLC Calculation Conditions Sheet (Std. calc)
[5 empty] | Indiv. Calc | Individual calculation |  | --> Input WLC Calculation Conditions Sheet (Indiv. calc)
2) Entry for individual building type
[1] Floor area of each building type | [5 empty] | common | ratio | Residential
Offices | 7000 | m2 Office | 7000 | ㎡ | Offices | 7000 | 1 |  |  | 1 | Offices, | 事務所 | 事務所 | 7000
|  | Government buildings |  | ㎡ | [5 empty] | 0 |  |  | 官公庁 | 0
|  | research institutes |  | ㎡ | [8 empty] | 研究施設 | 0
Schools | 0 | m2 Kindergartens/ nursery schools |  | ㎡ | Schools | 0 | 0 |  |  | 0 |  | 学校等 | 幼稚園・保育園 | 0
|  | Elementary/junior high schools (Hokkaido) |  | ㎡ | [5 empty] | 0 |  |  | 小中（北海道） | 0
|  | Elementary/junior high schools (other than Hokkaido) |  | ㎡ | [5 empty] | 0 |  |  | 小中（その他） | 0
|  | High schools |  | ㎡ | [5 empty] | 0 |  |  | 高校 | 0
|  | Universities/technical colleges |  | ㎡ | [5 empty] | 0 |  |  | 大学・専門学校 | 0
Retailers | 0 | m2 Department stores, supermarkets |  | ㎡ | Retailers | 0 | 0 |  |  | 0 |  | 物販店舗等 | デパート・スーパー | 0
|  | convenience store |  | ㎡ | [8 empty] | コンビニエンスストア | 0
|  | electronics retailers, |  | ㎡ | [8 empty] | 家電量販店 | 0
|  | Other stores |  | ㎡ | [5 empty] | 0 |  |  | その他物販 | 0
Restaurants |  | m2 |  |  | Restaurants | 0 | 0 |  |  | 0 |  | 飲食店 |  | 0
Halls | 0 | m2 Theatres/halls |  | ㎡ | Halls | 0 | 0 |  |  | 0 |  | 集会所等 | 劇場・ホール | 0
|  | Exhibition facilities |  | ㎡ | [5 empty] | 0 |  |  | 展示施設 | 0
|  | Sports facilities |  | ㎡ | [5 empty] | 0 |  |  | スポーツ施設 | 0
Factories |  | ㎡ Area subjected for energy efficiency calc |  | ㎡ | Factories | 0 | 0 |  |  | 0 |  | 工場 |  | 0
Hospitals |  | ㎡ |  |  | Hospitals | 0 | 0 | 0 |  | 0 |  | 病院 |  | 0
Hotels |  | ㎡ |  |  | Hotels | 0 | 0 | 0 |  | 0 |  | ホテル・旅館 |  | 0
Non-Apartment Subtotal | 7000 | ㎡ | [7 empty] | 0
Apartments |  | m2 Dwelling area | 0 | ㎡ | Apartments | 0 | 0 | 0 |  | 0 |  | 集合住宅 | 専有部 | 0
|  | Common area (except guest rooms) |  | ㎡ | [8 empty] | 共用部 | 0
[5 empty] | Total | 7000 | 1 | 0
[2] Ratio of Dwelling & Accommodation areas | [10 empty] | Offices,
n Proportion of gross floor area designated as bed rooms in Hospital
n Proportion of gross floor area designated as guest rooms in Hotel
n Proportion of gross floor area designate as dwelling units in Apartment |  |  |  | 0
3) Results Output
Score Sheet | ●Score
Assessment Result Sheet | ●Result | ●Result (2-1 SDGs) | ●WLC Calculation
WLC Calc Conditions Sheet | ●Standard Calculation |  | ●Individual Calculation
Building type | Types included
Offices | Offices, government buildings, post offices, etc.
Schools | Elementary schools, junior high schools, high schools, universities, technical colleges, higher vocational school and other school types, etc.
Retailers | Department stores, supermarkets, etc.
Restaurants | Restaurants, canteens, cafes, etc.
Halls | Auditoriums, halls, libraries, museums, bowling lanes, gymnasiums, theaters, movie theaters, exhibition facilities, etc.
Factories | Factories, garages, warehouses, spectator stands, wholesale markets, computer rooms, etc.
Hospitals | Hospitals, homes for elderly, welfare homes for the handicapped, etc.
Hotels | Hotels, inn, etc.
Apartments | Apartments (detached houses are not applied)
Note on B41: Fill in if the assessment is confirmed by third party.
Note on F71: Input the ratio, in the range 0.00-1.00

## Result
←
[7 empty] | n Manual: |  |  | CASBEE for Building Design (New Construction) 2024 Edition | n Software: | CASBEE-BD_NCe_2024_v1.21 |  |  | BEE rank |  |  | 2-3 Results of Major categories (radar chart)
1-1 Building Outline | [9 empty] | 1-2 Appearance |  |  |  |  | SQ | 3 |  |  | radar chart | background | 4 | 2 | Score(RoundDown) | std
Building Name |  | XXX Building |  |  |  | Number of Floors |  | + XX F | [6 empty] | SLR | #VALUE! |  | Q2 | Q2 Quality of Service | 5 | 4 | 2 | 3 | 3
Location |  | XX City, XX Prefecture |  |  |  | Structure |  | RC | [6 empty] | Q | 50 |  | Q3 | Q3 Outdoor Environment on Site | 5 | 4 | 2 | 3 | 3
Area / Zone |  | Commercial zone |  |  |  | Occupancy |  | XX | people | [5 empty] | L | #VALUE! |  | LR3 | LR3 Off-site Environment | 5 | 4 | 2 | #VALUE! | 3
Regional classification |  | Zone 3 |  |  |  | Annual Occupancy |  | XXX | hrs./yr. (assumed) | [5 empty] | BEE | #VALUE! |  | LR2 | LR2 Resources & Materials | 5 | 4 | 2 | 3 | 3
Building Type |  | Offices, |  |  |  | Assessment phase |  | Execution design stage |  |  | Exterior perspective etc. |  |  |  | BEE(Round) | #VALUE! |  | LR1 | LR1 Energy | 5 | 4 | 2 | 4 | 3
Completion |  | 2027-03-01 |  | Scheduled |  | Assessment date |  | 2025-07-08 | [6 empty] | Rank(red star) | #VALUE! |  | Q1 | Q1 Indoor Environment | 5 | 4 | 2 | 3 | 3
使用期間 |  | 2016年６月～８月 | [12 empty] | (blank star) | #VALUE!
Site Area |  |  | 5000 | ㎡ |  | Assessor |  | XXXXX |  |  | unlock the sheet's protection.
Construction Area |  |  | 4000 | ㎡ |  | Date of approval |  | 2025-07-10
Gross Floor Area |  |  | 7000 | ㎡ |  | Approved by |  | XXXXX
改修工事期間 |  | RN使用欄 | [7 empty] | 改修対象項目 | 躯体 | RN使用欄
改修目的 |  | RN使用欄 | [8 empty] | 外装 | RN使用欄
改修後の想定使用年数 |  | RN使用欄 | [8 empty] | 内装 | RN使用欄
現在までの主な改修履歴 |  | RN使用欄 | [8 empty] | 設備 | RN使用欄
2-1 Built Environment Efficiency (rank & chart) | [5 empty] | 2-2 WLC (Global Warming Impact Chart) |  |  |  | 2-3 Results of Major categories (radar chart) |  |  |  |  | BEEグラフ | 基準 | 評価 | 原点
[15 empty] | BEEの分母側(L) |  | #VALUE! | 0 |  | X目盛線 |  |  | Y目盛線 |  | 非表示
| #VALUE! | [13 empty] | BEEの分子側(Q) |  | 50 | 0 |  | 50 | 50 |  | 0 | 100
[15 empty] | 0 | #VALUE! | #VALUE! | 0.1 |  | 0 | 100 |  | 50 | 50
[15 empty] | 0 | 0 | 50 | 50
Std. Calc
[15 empty] | BEE | X | 0 | 16.6667 | 33.3333 | 50 | 66.6667 | 83.3333 | 100
[16 empty] | S | 100 | 100 | 100 | 100 | 100 | 100 | 100
[15 empty] | 3 | A | 50 | 50 | 100 | 100 | 100 | 100 | 100
[15 empty] | 1.5 | B+ | 0 | 25 | 50 | 75 | 100 | 100 | 100
[15 empty] | 1 | B | 0 | 16.6667 | 33.3333 | 50 | 66.6667 | 83.3333 | 100
[15 empty] | 0.5 | B- | 0 | 8.3333 | 16.6667 | 25 | 33.3333 | 41.6667 | 50
[15 empty] | Rank(green star) | #VALUE! | #VALUE! | Std. Calc |  | Std. Calc | This chart indicates rough estimate of WLC of evaluated building in LR3.1 "Consideration of Global Warming" compared with that of reference building.
[6 empty] | This chart indicates rough estimate of WLC of evaluated building in LR3.1 "Consideration of Global Warming" compared with that of reference building. | [8 empty] | (blank star) | #VALUE! |  |  |  | Indiv. Calc | This chart indicates rough estimate of WLC calculated by the assessor (individual calculation)of evaluated building compared with that of reference building. Refer "WLC calculation conditions sheet (Indiv. calc)" to see the assumptions for the conditions.
[16 empty] | UC | EC-UC | OC | ｵﾝｻｲﾄ | ｵﾌｻｲﾄ
[15 empty] | WLC(kg-CO2/ym2) | Construction | Repair, renewal/demolition | Operation | On-site | Off-site |  | ％ | Sum
2-4 Assessment results of Medium-level categories (bar chart) | [14 empty] | Ref | 18.22 | 20.11 | #VALUE! |  |  |  | 100% | #VALUE!
Q Environmental Quality | [10 empty] | Score of Q= | 3 |  |  | Subjest1 | 18.22 | 20.11 | #VALUE! |  |  |  | #VALUE! | #VALUE! | N.A.
| Q1 Indoor Environment |  |  |  |  | Q2 Quality of Service |  |  |  | Q3 Outdoor Environment on Site |  |  |  |  | Subjest2 |  |  |  | #VALUE! |  |  | #VALUE! | #VALUE! | N.A.
[5 empty] | 3 |  |  |  | 3 |  |  |  | 3 |  | Subjest3 |  |  |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | N.A.
[16 empty] | Score(Round Down) | Score |  | Score(Round Down) | Score |  | Score(Round Down) | Score
[15 empty] | Q1 Indoor Environment | 3 | 3 | Q2 Quality of Service | 3 | 3 | Q3 Outdoor Environment on Site | 3 | 3
[16 empty] | Score(Round Down) | NA |  | Score(Round Down) | NA |  | Score(Round Down) | NA
[15 empty] | 音環境 | 3 |  | 機能性 | 3 |  | 生物資源 | 3
[15 empty] | 温熱環境 | 3 |  | 耐用性・信頼性 | 3 |  | まちなみ景観 | 3
[15 empty] | 光・視環境 | 3 |  | 対応性･更新性 | 3 |  | 地域性・文化 | 3
LR Environmental Load Reduction | [10 empty] | Score of LR= | #VALUE! |  |  | 空気質環境 | 3
| LR1 Energy Energy |  |  |  |  | LR2 Resources & Materials |  |  |  | LR3 Off-site Environment
[5 empty] | 4 |  |  |  | 3 |  |  |  | #VALUE!
[16 empty] | Score(Round Down) | Score |  | Score(Round Down) | Score |  | Score(Round Down) | Score
[15 empty] | LR1 Energy | 4 | 4 | LR2 Resources & Materials | 3 | 3 | LR3 Off-site Environment | #VALUE! | #VALUE!
[16 empty] | Score(Round Down) | NA |  | Score(Round Down) | NA |  | Score(Round Down) | NA
[15 empty] | 熱負荷抑制 | 3 |  | 水資源 | 3 |  | 地球温暖化への配慮 | #VALUE! | #VALUE!
[15 empty] | 自然ｴﾈﾙｷﾞｰ | 3 |  | 非再生性材料の削減 | 3 |  | 地域環境への配慮 | 3
[15 empty] | 設備の効率的利用 | 5 |  | 汚染物質回避 | 3 |  | 周辺環境への配慮 | 3
[15 empty] | 運用ﾏﾈｼﾞﾒﾝﾄ | 3
3 Design considerations
General | [9 empty] | Other
Q1 Indoor Environment | [5 empty] | Q2 Quality of Service |  |  |  | Q3 Outdoor Environment on Site
LR1 Energy | [5 empty] | LR2 Resources & Materials |  |  |  | LR3 Off-site Environment
（3） 建築物の総合的な環境性能とは別枠の重要評価項目 | [12 empty] | 注3
（3）-1 建築物の代表的な環境負荷に関する定量的な評価指標 | [12 empty] | ＜実施設計段階、竣工段階で詳細な評価を行う場合に記入＞
|  |  | 年間延床面積あたり指標 |  |  | 人・時間あたり指標 |  | 年間延床面積あたり削減量 |  | 削減率 ％ |  |  | %
| 運用エネルギー消費量 |  |  | ＭＪ/年㎡ |  |  | ＭＪ/人時 |  | ＭＪ/年㎡
| 運用CO2排出量 |  |  | kg-CO2/年㎡ |  |  | kg-CO2/人時 |  | kg-CO2/年㎡
| 水消費量 |  |  | m3/年㎡ |  |  | m3/人時 |  | m3/年㎡
| LCCO2排出量 |  |  | kg-CO2/年㎡ |  |  | kg-CO2/人時 |  | kg-CO2/年㎡
| LC廃棄物量 |  |  | ｔ/年㎡ |  |  | ｔ/人時 |  | ｔ/年㎡
| LC資源消費量 |  |  | ｔ/年㎡ |  |  | ｔ/人時 |  | ｔ/年㎡
（3）-2 デザインプロセスの評価
設計段階 | [7 empty] | 建設段階
| 有資格者による設計 | [6 empty] | 環境管理計画
| 凡例 Q： | Quality | L：Load |  |  | LR：Load Reduction |  | SQ：Score of Q category |  | SLR：Score of LR category |  | BEE：Building Environmental Efficiency
| 備考 注1： | 当該対象区における標準的な計画の得点が３点。ＮＡは評価対象外とした項目を示す。敷地選定に関わる評価は対象外。
| 注2： | Qは、環境品質・性能（Q）のスコアSQ(Q-1、Q-2、Q-3のスコアにそれぞれの重み係数を乗じた合計値）から算定。
Lは、環境負荷低減性（LR)のスコアSLR（LR-1、LR-2、LR-3のスコアにそれぞれの重み係数を乗じた合計値）から算定。
| 注3： | (3)の評価はオプションとし、実施設計段階および竣工段階で可能な範囲で記入する。
BEE =
S: ★★★★★ A: ★★★★ B+: ★★★ B-: ★★ C: ★
30%: ☆☆☆☆☆ 60%: ☆☆☆☆ 80%: ☆☆☆ 100%: ☆☆ 100% < ☆
（ kg-CO2eqe/yr-m2 ）
Environmental Quality Q
Environmental Load L
1.Reference value
2.Building-related
initiatives
3.Above initiatives + other on-site measures
4.Above initiatives + other off-site measures
Noise &
Acoustics
Thermal
Comfort
Lighting &
Illumination
Air Quality
Service
Ability
Durability
& Reliability
Flexibility
& Adaptability
Preservation & Creation of Biotope
Townscape & Landscape
Local Characteristics & Outdoor Amenity
Building Thermal Load
Natural Energy (Direct use)
Efficiency in Building Service
System
Efficient Operation
Initiatives
Water Resources
Reduction of Non Renewable Material use
Materials with Low Health Risks
Global Warming
Local environment
Surrounding Environment
Score of LR1 =
Score of LR2 =
Score of LR3 =
n CASBEE: Comprehensive Assessment System for Built Environment Efficiency
n Q: Quality (environmental quality of building); L: Load (environmental load of building); LR: Load Reduction (environmental load reduction of building); BEE: Built Environment Efficiency
n "Whole Life Carbon (WLC)" is the total GHG emitted by a building during its entire life from the production of materials and construction of the building to occupation by the users, repairs, and demolition/disposal. Here it is displayed as annual WLC calculated by dividing total emissions by the building lifespan.
n WLC of evaluated building is calculated almost automatically from the results (scoring levels) of some assessment items, in Q2, LR1 and LR2 by using its lifespan, energy performance and material efficiency.
n For WLC calculation conditions, refer to the WLC Calculation Condition Sheet.

## Result(2-3SDGs)
←
[7 empty] | n Manual: |  |  | CASBEE for Building Design (New Construction) 2024 Edition | n Software: | CASBEE-BD_NCe_2024_v1.21 |  |  | BEE rank |  |  | 2-3 Results of Major categories (radar chart)
1-1 Building Outline | [9 empty] | 1-2 Appearance |  |  |  |  | SQ | 3 |  |  | radar chart | background | 4 | 2 | Score(Round Down) | std
Building Name |  | XXX Building |  |  |  | Number of Floors |  | + XX F | [6 empty] | SLR | #VALUE! |  | Q2 | Q2 Quality of Service | 5 | 4 | 2 | 3 | 3
Location |  | XX City, XX Prefecture |  |  |  | Structure |  | RC | [6 empty] | Q | 50 |  | Q3 | Q3 Outdoor Environment on Site | 5 | 4 | 2 | 3 | 3
Area / Zone |  | Commercial zone |  |  |  | Occupancy |  | XX | people | [5 empty] | L | #VALUE! |  | LR3 | LR3 Off-site Environment | 5 | 4 | 2 | #VALUE! | 3
Regional classification |  | Zone 3 |  |  |  | Annual Occupancy |  | XXX | hrs./yr. (assumed) | [5 empty] | BEE | #VALUE! |  | LR2 | LR2 Resources & Materials | 5 | 4 | 2 | 3 | 3
Building Type |  | Offices, |  |  |  | Assessment phase |  | Execution design stage |  |  | Exterior perspective etc. |  |  |  | BEE(Round) | #VALUE! |  | LR1 | LR1 Energy | 5 | 4 | 2 | 4 | 3
Completion |  | 2027-03-01 |  | Scheduled |  | Assessment date |  | 2025-07-08 | [6 empty] | Rank(red star) | #VALUE! |  | Q1 | Q1 Indoor Environment | 5 | 4 | 2 | 3 | 3
使用期間 |  | 2016年６月～８月 | [12 empty] | (blank star) | #VALUE!
Site Area |  |  | 5000 | ㎡ |  | Assessor |  | XXXXX |  |  | unlock the sheet's protection.
Construction Area |  |  | 4000 | ㎡ |  | Date of approval |  | 2025-07-10
Gross Floor Area |  |  | 7000 | ㎡ |  | Approved by |  | XXXXX
改修工事期間 |  | RN使用欄 | [7 empty] | 改修対象項目 | 躯体 | RN使用欄
改修目的 |  | RN使用欄 | [8 empty] | 外装 | RN使用欄
改修後の想定使用年数 |  | RN使用欄 | [8 empty] | 内装 | RN使用欄
現在までの主な改修履歴 |  | RN使用欄 | [8 empty] | 設備 | RN使用欄
2-1 Built Environment Efficiency (rank & chart) | [5 empty] | 2-2 WLC (Global Warming Impact Chart) |  |  |  | 2-3 Built Environment SDGs Checklist |  |  |  |  | BEEグラフ | 基準 | 評価 | 原点
[15 empty] | BEEの分母側(L) |  | #VALUE! | 0 |  | X目盛線 |  |  | Y目盛線
| #VALUE! | [13 empty] | BEEの分子側(Q) |  | 50 | 0 |  | 50 | 50 |  | 0 | 100
[15 empty] | 0 | #VALUE! | #VALUE! | 0.1 |  | 0 | 100 |  | 50 | 50
[15 empty] | 0 | 0 | 50 | 50
Std. Calc
[15 empty] | BEE | X | 0 | 16.6667 | 33.3333 | 50 | 66.6667 | 83.3333 | 100
[16 empty] | S | 100 | 100 | 100 | 100 | 100 | 100 | 100
[15 empty] | 3 | A | 50 | 50 | 100 | 100 | 100 | 100 | 100
[15 empty] | 1.5 | B+ | 0 | 25 | 50 | 75 | 100 | 100 | 100
[15 empty] | 1 | B | 0 | 16.6667 | 33.3333 | 50 | 66.6667 | 83.3333 | 100
[15 empty] | 0.5 | B- | 0 | 8.3333 | 16.6667 | 25 | 33.3333 | 41.6667 | 50
[15 empty] | Rank(green star) | #VALUE! | #VALUE! | Std. Calc |  | Std. Calc | This chart indicates rough estimate of WLC of evaluated building in LR3.1 "Consideration of Global Warming" compared with that of reference building.
[6 empty] | This chart indicates rough estimate of WLC of evaluated building in LR3.1 "Consideration of Global Warming" compared with that of reference building. | [8 empty] | (blank star) | #VALUE! |  |  |  | Indiv. Calc | This chart indicates rough estimate of WLC calculated by the assessor (individual calculation)of evaluated building compared with that of reference building. Refer "WLC calculation conditions sheet (Indiv. calc)" to see the assumptions for the conditions.
[10 empty] | * SDG 1,2,10,14,16 efforts are consolidated into other goals. |  |  |  |  | WLC(kg-CO2/ym2) | Construction | Repair, renewal/demolition | Operation | On-site | Off-site |  | ％ | Sum |  |  | スコア | 2-3 Built Environment SDGs Checklist
2-4 Assessment results of Medium-level categories (bar chart) | [14 empty] | Ref | 18.22 | 20.11 | #VALUE! | 0 | 0 | 0 | 100% | #VALUE! |  | ゴール3 | 2.1429 | implemented
Q Environmental Quality | [10 empty] | Score of Q= | 3 |  |  | Subjest1 | 18.22 | 20.11 | #VALUE! | 0 | 0 | 0 | #VALUE! | #VALUE! | N.A. | ゴール4 | 2
| Q1 Indoor Environment |  |  |  |  | Q2 Quality of Service |  |  |  | Q3 Outdoor Environment on Site |  |  |  |  | Subjest2 | 0 | 0 | 0 | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | N.A. | ゴール5 | 2
[5 empty] | 3 |  |  |  | 3 |  |  |  | 3 |  | Subjest3 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | N.A. | ゴール6 | 1.7857 | SDGs Rank | #VALUE!
[25 empty] | ゴール7 | #VALUE! | SDGs Rank(Ring) | #VALUE!
[16 empty] | Score(Round Down) | Score |  | Score(Round Down) | Score |  | Score(Round Down) | Score |  | ゴール8 | 2 | (Blank Ring) | #VALUE!
[15 empty] | Q1 Indoor Environment | 3 | 3 | Q2 Quality of Service | 3 | 3 | Q3 Outdoor Environment on Site | 3 | 3 |  | ゴール9 | 1.75
[25 empty] | ゴール11 | 1.8833
[16 empty] | Score(Round Down) | NA |  | Score(Round Down) | NA |  | Score(Round Down) | NA |  | ゴール12 | #VALUE!
[15 empty] | 音環境 | 3 |  | 機能性 | 3 |  | 生物資源 | 3 |  |  | ゴール13 | #VALUE!
[15 empty] | 温熱環境 | 3 |  | 耐用性・信頼性 | 3 |  | まちなみ景観 | 3 |  |  | ゴール15 | 1.375
[15 empty] | 光・視環境 | 3 |  | 対応性･更新性 | 3 |  | 地域性・文化 | 3 |  |  | ゴール17 | 2.1667
LR Environmental Load Reduction | [10 empty] | Score of LR= | #VALUE! |  |  | 空気質環境 | 3
| LR1 Energy Energy |  |  |  |  | LR2 Resources & Materials |  |  |  | LR3 Off-site Environment
[5 empty] | 4 |  |  |  | 3 |  |  |  | #VALUE!
[16 empty] | Score(Round Down) | Score |  | Score(Round Down) | Score |  | Score(Round Down) | Score
[15 empty] | LR1 Energy | 4 | 4 | LR2 Resources & Materials | 3 | 3 | LR3 Off-site Environment | #VALUE! | #VALUE!
[16 empty] | Score(Round Down) | NA |  | Score(Round Down) | NA |  | Score(Round Down) | NA
[15 empty] | 熱負荷抑制 | 3 |  | 水資源 | 3 |  | 地球温暖化への配慮 | #VALUE! | #VALUE!
[15 empty] | 自然ｴﾈﾙｷﾞｰ | 3 |  | 非再生性材料の削減 | 3 |  | 地域環境への配慮 | 3
[15 empty] | 設備の効率的利用 | 5 |  | 汚染物質回避 | 3 |  | 周辺環境への配慮 | 3
[15 empty] | 運用ﾏﾈｼﾞﾒﾝﾄ | 3
3 Design considerations
General | [9 empty] | Other
Q1 Indoor Environment | [5 empty] | Q2 Quality of Service |  |  |  | Q3 Outdoor Environment on Site
LR1 Energy | [5 empty] | LR2 Resources & Materials |  |  |  | LR3 Off-site Environment
（3） 建築物の総合的な環境性能とは別枠の重要評価項目 | [12 empty] | 注3
（3）-1 建築物の代表的な環境負荷に関する定量的な評価指標 | [12 empty] | ＜実施設計段階、竣工段階で詳細な評価を行う場合に記入＞
|  |  | 年間延床面積あたり指標 |  |  | 人・時間あたり指標 |  | 年間延床面積あたり削減量 |  | 削減率 ％ |  |  | %
| 運用エネルギー消費量 |  |  | ＭＪ/年㎡ |  |  | ＭＪ/人時 |  | ＭＪ/年㎡
| 運用CO2排出量 |  |  | kg-CO2/年㎡ |  |  | kg-CO2/人時 |  | kg-CO2/年㎡
| 水消費量 |  |  | m3/年㎡ |  |  | m3/人時 |  | m3/年㎡
| LCCO2排出量 |  |  | kg-CO2/年㎡ |  |  | kg-CO2/人時 |  | kg-CO2/年㎡
| LC廃棄物量 |  |  | ｔ/年㎡ |  |  | ｔ/人時 |  | ｔ/年㎡
| LC資源消費量 |  |  | ｔ/年㎡ |  |  | ｔ/人時 |  | ｔ/年㎡
（3）-2 デザインプロセスの評価
設計段階 | [7 empty] | 建設段階
| 有資格者による設計 | [6 empty] | 環境管理計画
| 凡例 Q： | Quality | L: Load |  |  | LR: Load Reduction |  | SQ: Score of Q category |  | SLR: Score of LR category |  | BEE: Building Environmental Efficiency
| 備考 注1： | 当該対象区における標準的な計画の得点が３点。ＮＡは評価対象外とした項目を示す。敷地選定に関わる評価は対象外。
| 注2： | Qは、環境品質・性能（Q）のスコアSQ(Q-1、Q-2、Q-3のスコアにそれぞれの重み係数を乗じた合計値）から算定。
Lは、環境負荷低減性（LR)のスコアSLR（LR-1、LR-2、LR-3のスコアにそれぞれの重み係数を乗じた合計値）から算定。
| 注3： | (3)の評価はオプションとし、実施設計段階および竣工段階で可能な範囲で記入する。
BEE =
S: ★★★★★ A: ★★★★ B+: ★★★ B-: ★★ C: ★
30%: ☆☆☆☆☆ 60%: ☆☆☆☆ 80%: ☆☆☆ 100%: ☆☆ 100% < ☆
（ kg-CO2eq/yr-m2 ）
2.0
2.0
1.8
#VALUE!
2.0
1.8
1.9
#VALUE!
#VALUE!
1.4
2.2
2.1
3(Health)
4(Education)
5(Gender)
6(Water/Sanitation)
7(Energy)
8(Job/Economy)
9(Innovation)
11(Cities)
12(Consum./Prod.)
13(Climate action)
17(Partnerships)
15(Life on land)
Environmental Quality Q
Environmental Load L
1.Reference value
2.Building-related
initiatives
3.Above initiatives + other on-site measures
4.Above initiatives + other off-site measures
Noise &
Acoustics
Thermal
Comfort
Lighting &
Illumination
Air Quality
Service
Ability
Durability
& Reliability
Flexibility
& Adaptability
Preservation & Creation of Biotope
Townscape & Landscape
Local Characteristics & Outdoor Amenity
Building Thermal Load
Efficiency in Building Service
System
Efficient Operation
Initiatives
Water Resources
Reduction of Non Renewable Material use
Materials with Low Health Risks
Global Warming
Local environment
Surrounding Environment
Score of LR1 =
Score of LR2 =
Score of LR3 =
n CASBEE: Comprehensive Assessment System for Built Environment Efficiency
n Q: Quality (environmental quality of building); L: Load (environmental load of building); LR: Load Reduction (environmental load reduction of building); BEE: Built Environment Efficiency
n "Whole Life Carbon (WLC)" is the total GHG emitted by a building during its entire life from the production of materials and construction of the building to occupation by the users, repairs, and demolition/disposal. Here it is displayed as annual WLC calculated by dividing total emissions by the building lifespan.
n WLC of evaluated building is calculated almost automatically from the results (scoring levels) of some assessment items, in Q2, LR1 and LR2 by using its lifespan, energy performance and material efficiency.
n For WLC calculation conditions, refer to the WLC Calculation Condition Sheet.
Natural Energy (Direct use)

## Consider
n Considerations in environmental design |  |  | n Building Name | XXX Building
Considerations in design
General | Describe briefly comprehensive concept of environmental design of the building. | Describe briefly comprehensive concept of environmental design of the building.
Q1 Indoor Environment | Describe briefly considerations for Q1 Indoor Environment of the building. | Describe briefly considerations for Q1 Indoor Environment of the building.
Q2 Quality of Service | Describe briefly considerations for Q2 Quality of Service of the building. | Describe briefly considerations for Q2 Quality of Service of the building.
Q3 Outdoor Environment on Site | Describe briefly considerations for Q3 Outdoor Environment on Site of the building. | Describe briefly considerations for Q3 Outdoor Environment on Site of the building.
LR1 Energy | Describe briefly considerations for LR1 Energy of the building. | Describe briefly considerations for LR1 Energy of the building.
LR2 Resources & Materials | Describe briefly considerations for LR2 Resources & Materials of the building. | Describe briefly considerations for LR2 Resources & Materials of the building.
LR3 Off-site Environment | Describe briefly considerations for LR3 Off-site Environment of the building. | Describe briefly considerations for LR3 Off-site Environment of the building.
Other | Describe briefly considerations for other than 6 categories above that is not assessed in CASBEE-NC, such as recycling activities at constriction site and preservation of historic buildings. | Describe briefly considerations for other than 6 categories above that is not assessed in CASBEE-NC, such as recycling activities at constriction site and preservation of historic buildings.

## 複合用途 (hidden)
重み係数 | [11 empty] | CASBEE for Building Design (New Construction) 2024 Edition | [19 empty] | ※「対象外」を選択の場合は、「0（ゼロ）」を入力 | [12 empty] | 重み係数（複数用途建物） | [12 empty] | 重み係数（既定）
[12 empty] | XXX Building | [19 empty] | 用途別スコア | [25 empty] | 2 |  | NC | [13 empty] | 0. 既存 | [15 empty] | １．基本設計 | [15 empty] | ２．実施・竣工段階 | [16 empty] | ３．短期使用 | [15 empty] | ４．ｲﾝﾃﾘｱｽﾍﾟｰｽ
|  | 補正後 |  | 補正前 |  | 補正前計 |  | 対象外の選択 |  | 既定重み |  | スコアシート | [19 empty] | 建物全体・共用部 | [9 empty] | 住居・宿泊部 |  |  | 補正後 | 補正前 | 補正前計 | 建物全体・共用部 | [12 empty] | 建物全体・共用部 | [9 empty] | 住居・宿泊部 | [5 empty] | 建物全体・共用部 | [9 empty] | 住居・宿泊部 | [5 empty] | 建物全体・共用部 | [9 empty] | 住居・宿泊部 | [5 empty] | 建物全体・共用部 | [9 empty] | 住居・宿泊部 | [6 empty] | 建物全体・共用部 | [9 empty] | 住居・宿泊部 | [5 empty] | 建物全体・共用部 | [9 empty] | 住居・宿泊部
|  | 全体・共有 | 住居・宿泊 | 全体・共有 | 住居・宿泊 | 全体・共有 | 住居・宿泊 | 全体・共有 | 住居・宿泊 | 全体・共有 | 住居・宿泊 | [5 empty] | 建物全体・共用部分 | 住居・宿泊部分 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 小中高 | 病院 | ホテル | 集合住宅 | 病院o | ホテルo | 集合住宅o | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 小中高 | 病院 | ホテル | 集合住宅 | 病院o | ホテルo | 集合住宅o | 全体・共有 | 全体・共有 |  | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 小中高 | 病院 | ホテル | 集合住宅 |  | 項目 | 項目名 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 小中高 | 病院 | ホテル | 集合住宅 | 病院o | ホテルo | 集合住宅o |  | 項目 | 項目名 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 小中高 | 病院 | ホテル | 集合住宅 | 病院o | ホテルo | 集合住宅o |  | 項目 | 項目名 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 小中高 | 病院 | ホテル | 集合住宅 | 病院o | ホテルo | 集合住宅o |  | 項目 | 項目名 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 小中高 | 病院 | ホテル | 集合住宅 | 病院o | ホテルo | 集合住宅o |  |  | 項目 | 項目名 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 小中高 | 病院 | ホテル | 集合住宅 | 病院o | ホテルo | 集合住宅o |  | 項目 | 項目名 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 小中高 | 病院 | ホテル | 集合住宅 | 病院o | ホテルo | 集合住宅o
| 延面積比率 | 1 | 0 | [8 empty] | 配慮項目 |  |  |  |  | 評価点 | 評価点 | [13 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 延面積 | 延面積比率 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Q | 建築物の環境品質 |  |  |  |  | #REF! | #REF! |  |  |  |  | Ｑ 建築物の環境品質 | [34 empty] | #REF! | [7 empty] | 1 | 1 | 1 |  | Q | 住居宿泊・共用部面積比率 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | Q |  | 建築物の環境品質 | [13 empty] | Q |  | 建築物の環境品質 | [13 empty] | Q |  | 建築物の環境品質 | [14 empty] | Q |  | 建築物の環境品質 | [13 empty] | Q |  | 建築物の環境品質 | 0
Q1 | 室内環境 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.4 | 0 | Q1 | 室内環境 | [18 empty] | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 小中高 | 病院 | ホテル | 集合住宅 | 病院o | ホテルo | 集合住宅o | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Q1 | Q | 室内環境 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | Q1 | Q | 室内環境 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | Q1 | Q | 室内環境 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | Q1 | Q | 室内環境 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  |  | Q1 | Q | 室内環境 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | Q1 | Q | 室内環境 | 0.5
1 | 音環境 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.15 | 0 | 1 | 音環境 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1 | Q1 | 音環境 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 1 | Q1 | 音環境 | 0.15 | 0.15 | 0.15 | 0.15 | 0.23 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 |  |  |  | 1 | Q1 | 音環境 | 0.15 | 0.15 | 0.15 | 0.15 | 0.23 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 |  |  |  | 1 | Q1 | 音環境 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 |  |  |  |  | 1 | Q1 | 音環境 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 1 | Q1 | 音環境 | 0.15 | bar: 事務所 to ホテル
1.1 | 室内騒音レベル | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.4 | 0 |  | 1.1 | 室内騒音レベル |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | [10 empty] | 4 | 5 |  |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.1 | Q1 1 | 室内騒音レベル | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.5 | 1.1 | Q1 1 | 騒音 | 0.4 | 0.4 | 0.8 | 0.4 | 0.8 | 0.5 | 0.4 | 0.4 | 0.8 | 0.8 | 0.5 | 0.4 | 0.4 | 1.1 | Q1 1 | 騒音 |  |  |  |  | 0.4 | [8 empty] | 1.1 | Q1 1 | 室内騒音レベル | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.5 |  | 1.1 | Q1 1 | 室内騒音レベル | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | Q1 1 | 室内騒音レベル | 1
1.1.1 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 1 | 室内騒音レベル |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.1.1 | Q1 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1.1 | Q1 1.1 | 室内騒音レベル | 0.4 | 1 | 1 | 1 | 1 | 0.4 | 1 | 0.4 | 1 | 1 | 0.4 | 1 | 1 | 1.1.1 | Q1 1.1 | 室内騒音レベル |  |  |  |  | 1 | [8 empty] | 1.1.1 | Q1 1.1 | [15 empty] | 1.1.1 | Q1 1.1 | [14 empty] | 1.1.1 | Q1 1.1 |  | 0
1.1.2 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 2 | 設備騒音対策 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.1.2 | Q1 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1.2 | Q1 1.1 | 設備騒音対策 | 0.6 |  |  |  |  | 0.6 |  | 0.6 |  |  | 0.6 |  |  | 1.1.2 | Q1 1.1 | 設備騒音対策 | [13 empty] | 1.1.2 | Q1 1.1 | [15 empty] | 1.1.2 | Q1 1.1 | [14 empty] | 1.1.2 | Q1 1.1 |  | 0
1.2 | 遮音 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.4 | 0 |  | 1.2 | 遮音 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.2 | Q1 1 | 遮音 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.5 | 1.2 | Q1 1 | 遮音 | 0.4 | 0.4 |  | 0.4 |  | 0.5 | 0.4 | 0.4 |  |  | 0.5 | 0.4 | 0.4 | 1.2 | Q1 1 | 遮音 | 0.7 | 0.7 | 0.7 | 0.7 | 0.4 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 0.7 | 0.7 | 1 | 1.2 | Q1 1 | 遮音 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.5 |  | 1.2 | Q1 1 | 遮音 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 1 | 0.67 | 0.67 | 1 | 1.2 | Q1 1 | 遮音 | 0 | bar: 事務所 to ホテル
1.2.1 | 開口部遮音性能 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.6 | 0 |  |  | 1 | 開口部遮音性能 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.2.1 | Q1 1.2 | 開口部遮音性能 | 0.6 | 0.3 | 1 | 0.6 | 1 | 0.6 | 0.3 | 0.4 | 1 | 1 | 0.3 | 0.3 | 0.3 | 1.2.1 | Q1 1.2 | 開口部遮音性能 | [13 empty] | 1.2.1 | Q1 1.2 | 開口部遮音性能 | 0.6 | 0.4 | 1 | 0.6 | 1 | 0.6 | 0.4 | 0.4 | 1 | 1 | 0.3 | 0.3 | 0.3 | 1.2.1 | Q1 1.2 | 開口部遮音性能 | 0.6 | 0.3 | 1 | 0.6 | 1 | 0.6 | 0.3 | 0.4 | 1 | 1 | 0.3 | 0.3 | 0.3 |  | 1.2.1 | Q1 1.2 | 開口部遮音性能 | 0.6 | 0.3 | 1 | 0.6 | 1 | 0.6 | 0.3 | 0.4 | 1 | 1 | 0.3 | 0.3 | 0.3 | 1.2.1 | Q1 1.2 | 開口部遮音性能 | 0
1.2.2 | 界壁遮音性能 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.4 | 0 |  |  | 2 | 界壁遮音性能 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.2.2 | Q1 1.2 | 界壁遮音性能 | 0.4 | 0.3 | 0 | 0.4 | 0 | 0.4 | 0.3 | 0.6 | 0 | 0 | 0.3 | 0.3 | 0.3 | 1.2.2 | Q1 1.2 | 界壁遮音性能 | 1 | 0.4 |  | 1 |  | 1 | 0.4 | 0.4 |  |  | 1 | 0.4 | 0.4 | 1.2.2 | Q1 1.2 | 界壁遮音性能 | 0.4 | 0.3 |  | 0.4 |  | 0.4 | 0.3 | 0.6 |  |  | 0.3 | 0.3 | 0.3 | 1.2.2 | Q1 1.2 | 界壁遮音性能 | 0.4 | 0.3 |  | 0.4 |  | 0.4 | 0.3 | 0.6 |  |  | 0.3 | 0.3 | 0.3 |  | 1.2.2 | Q1 1.2 | 界壁遮音性能 | 0.4 | 0.3 | 0 | 0.4 | 0 | 0.4 | 0.3 | 0.6 | 0 | 0 | 0.3 | 0.3 | 0.3 | 1.2.2 | Q1 1.2 | 界壁遮音性能 | 0
1.2.3 | 界床遮音性能（軽量衝撃源） | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 3 | 界床遮音性能（軽量衝撃源） |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [10 empty] | 4 |  |  |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.2.3 | Q1 1.2 | 界床遮音性能（軽量衝撃源） | 0 | 0.2 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 1.2.3 | Q1 1.2 | 界床遮音性能（軽量衝撃源） |  | 0.3 |  |  |  |  | 0.3 | 0.6 |  |  |  | 0.3 | 0.3 | 1.2.3 | Q1 1.2 | 界床遮音性能（軽量衝撃源） |  | 0.15 |  |  |  |  | 0.15 |  |  |  | 0.2 | 0.2 | 0.2 | 1.2.3 | Q1 1.2 | 界床遮音性能（軽量衝撃源） |  | 0.2 |  |  |  |  | 0.2 |  |  |  | 0.2 | 0.2 | 0.2 |  | 1.2.3 | Q1 1.2 | 界床遮音性能（軽量衝撃源） | 0 | 0.2 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 1.2.3 | Q1 1.2 | 界床遮音性能（軽量衝撃源） | 0
1.2.4 | 界床遮音性能（重量衝撃源） | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 4 | 界床遮音性能（重量衝撃源） |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.2.4 | Q1 1.2 | 界床遮音性能（重量衝撃源） | 0 | 0.2 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 1.2.4 | Q1 1.2 | 界床遮音性能（重量衝撃源） |  | 0.3 |  |  |  |  | 0.3 |  |  |  |  | 0.3 | 0.3 | 1.2.4 | Q1 1.2 | 界床遮音性能（重量衝撃源） |  | 0.15 |  |  |  |  | 0.15 |  |  |  | 0.2 | 0.2 | 0.2 | 1.2.4 | Q1 1.2 | 界床遮音性能（重量衝撃源） |  | 0.2 |  |  |  |  | 0.2 |  |  |  | 0.2 | 0.2 | 0.2 |  | 1.2.4 | Q1 1.2 | 界床遮音性能（重量衝撃源） | 0 | 0.2 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 1.2.4 | Q1 1.2 | 界床遮音性能（重量衝撃源） | 0
1.3 | 吸音 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.2 | 0 |  | 1.3 | 吸音 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.3 | Q1 1 | 吸音 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0.2 | 0.2 | 0 | 1.3 | Q1 1 | 吸音 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 0.2 | 0.2 | 0.2 | 0.2 |  | 0.2 | 0.2 | 1.3 | Q1 1 | 吸音 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0.3 | 0.3 | 0 | 1.3 | Q1 1 | 吸音 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0.2 | 0.2 | 0 |  | 1.3 | Q1 1 | 吸音 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0 | 0.33 | 0.33 | 0 | 1.3 | Q1 1 | 吸音 | 0
2 | 温熱環境 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.35 | 0 | 2 | 温熱環境 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2 | Q1 | 温熱環境 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 2 | Q1 | 温熱環境 | 0.35 | 0.35 | 0.35 | 0.35 | 0.44 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 |  |  |  | 2 | Q1 | 温熱環境 | 0.35 | 0.35 | 0.35 | 0.35 | 0.44 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 |  |  |  | 2 | Q1 | 温熱環境 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 |  |  |  |  | 2 | Q1 | 温熱環境 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 2 | Q1 | 温熱環境 | 0.35 | bar: 事務所 to ホテル
2.1 | 室温制御 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.5 | 0 |  | 2.1 | 室温制御 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.1 | Q1 2 | 室温制御 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 2.1 | Q1 2 | 室温制御 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 2.1 | Q1 2 | 室温制御 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 2.1 | Q1 2 | 室温制御 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 2.1 | Q1 2 | 室温制御 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 2.1 | Q1 2 | 室温制御 | 0.5 | bar: 事務所 to ホテル
2.1.1 | 室温 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.375 | 0 |  |  | 1 | 室温 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.1.1 | Q1 2.1 | 室温 | 0.375 | 0.6 | 0.5 | 0.5 | 0.375 | 0.375 | 0.6 | 0.375 | 0.375 | 0.625 | 0.57143 | 0.57143 | 0.625 | 2.1.1 | Q1 2.1 | 室温設定 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 |  |  |  | 2.1.1 | Q1 2.1 | 室温 | 0.3 | 0.6 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.3 | 0.3 | 0.6 | 0.6 | 0.6 | 0.6 | 2.1.1 | Q1 2.1 | 室温 | 0.375 | 0.6 | 0.5 | 0.5 | 0.375 | 0.375 | 0.6 | 0.375 | 0.375 | 0.625 | 0.57143 | 0.57143 | 0.625 |  | 2.1.1 | Q1 2.1 | 室温 | 0.375 | 0.6 | 0.5 | 0.5 | 0.375 | 0.375 | 0.6 | 0.375 | 0.375 | 0.625 | 0.57143 | 0.57143 | 0.625 | 2.1.1 | Q1 2.1 | 室温 | 0.375
2.1.2 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 2 | 負荷変動・追従制御性 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.1.2 | Q1 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1.2 | Q1 2.1 | 負荷変動・追従制御性 |  | 0.2 | 0.2 | 0.2 | 0.3 |  | 0.2 | [6 empty] | 2.1.2 | Q1 2.1 | 負荷変動・追従制御性 | [13 empty] | 2.1.2 | Q1 2.1 | [15 empty] | 2.1.2 | Q1 2.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1.2 | Q1 2.1 |  | 0
2.1.3 | 外皮性能 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.25 | 0 |  |  | 2 | 外皮性能 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.1.3 | Q1 2.1 | 外皮性能 | 0.25 | 0.4 | 0.16667 | 0.16667 | 0.25 | 0.25 | 0.4 | 0.25 | 0.25 | 0.375 | 0.42857 | 0.42857 | 0.375 | 2.1.3 | Q1 2.1 | 外皮性能 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.6 | 2.1.3 | Q1 2.1 | 外皮性能 | 0.2 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 2.1.3 | Q1 2.1 | 外皮性能 | 0.25 | 0.4 | 0.16667 | 0.16667 | 0.25 | 0.25 | 0.4 | 0.25 | 0.25 | 0.375 | 0.42857 | 0.42857 | 0.375 |  | 2.1.3 | Q1 2.1 | 外皮性能 | 0.25 | 0.4 | 0.16667 | 0.16667 | 0.25 | 0.25 | 0.4 | 0.25 | 0.25 | 0.375 | 0.42857 | 0.42857 | 0.375 | 2.1.3 | Q1 2.1 | 外皮性能 | 0.25
2.1.4 | ゾーン別制御性 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.375 | 0 |  |  | 3 | ゾーン別制御性 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.1.4 | Q1 2.1 | ゾーン別制御性 | 0.375 | 0 | 0.33333 | 0.33333 | 0.375 | 0.375 | 0 | 0.375 | 0.375 | 0 | 0 | 0 | 0 | 2.1.4 | Q1 2.1 | ゾーン別制御性 | 0.3 |  | 0.2 | 0.2 | 0.2 | 0.3 | 0 | 0.3 | 0.3 |  |  |  |  | 2.1.4 | Q1 2.1 | ゾーン別制御性 | 0.5 |  | 0.5 | 0.5 | 0.5 | 0.5 |  | 0.5 | 0.5 |  |  |  |  | 2.1.4 | Q1 2.1 | ゾーン別制御性 | 0.375 |  | 0.33333 | 0.33333 | 0.375 | 0.375 |  | 0.375 | 0.375 | [5 empty] | 2.1.4 | Q1 2.1 | ゾーン別制御性 | 0.375 | 0 | 0.33333 | 0.33333 | 0.375 | 0.375 | 0 | 0.375 | 0.375 | 0 | 0 | 0 | 0 | 2.1.4 | Q1 2.1 | ゾーン別制御性 | 0.375
2.1.5 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 5 | 温度・湿度制御 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.1.5 | Q1 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1.5 | Q1 2.1 | 温度・湿度制御 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.3 | 0.3 |  | 2.1.5 | Q1 2.1 | 温度・湿度制御 | [13 empty] | 2.1.5 | Q1 2.1 | [15 empty] | 2.1.5 | Q1 2.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1.5 | Q1 2.1 |  | 0
2.1.6 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 6 | 個別制御 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.1.6 | Q1 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1.6 | Q1 2.1 | 個別制御 | [6 empty] | 0 |  |  |  | 0.2 | 0.2 | 0.4 | 2.1.6 | Q1 2.1 | 個別制御 | [13 empty] | 2.1.6 | Q1 2.1 | [15 empty] | 2.1.6 | Q1 2.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1.6 | Q1 2.1 |  | 0
2.1.7 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 7 | 時間外空調に対する配慮 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.1.7 | Q1 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1.7 | Q1 2.1 | 時間外空調に対する配慮 | 0.1 | 0.2 |  |  |  | 0.1 | 0.2 | 0.1 | 0.1 |  |  |  |  | 2.1.7 | Q1 2.1 | 時間外空調に対する配慮 | [13 empty] | 2.1.7 | Q1 2.1 | [15 empty] | 2.1.7 | Q1 2.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1.7 | Q1 2.1 |  | 0
2.1.8 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 8 | 監視システム |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.1.8 | Q1 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1.8 | Q1 2.1 | 監視システム |  |  | 0.1 | 0.1 |  |  | 0 | [6 empty] | 2.1.8 | Q1 2.1 | 監視システム | [13 empty] | 2.1.8 | Q1 2.1 | [15 empty] | 2.1.8 | Q1 2.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1.8 | Q1 2.1 |  | 0
2.2 | 湿度制御 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.2 | 0 |  | 2.2 | 湿度制御 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.2 | Q1 2 | 湿度制御 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 2.2 | Q1 2 | 湿度制御 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.2 | Q1 2 | 湿度制御 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 2.2 | Q1 2 | 湿度制御 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 2.2 | Q1 2 | 湿度制御 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 2.2 | Q1 2 | 湿度制御 | 0.2
2.3 | 空調方式（新築） | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.3 | 0 |  | 2.3 | 空調方式 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.3 | Q1 2 | 空調方式（新築） | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.3 | Q1 2 | [14 empty] | 2.3 | Q1 2 | 空調方式 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.3 | Q1 2 | 空調方式（新築） | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  | 2.3 | Q1 2 | 空調方式 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.3 | Q1 2 | 空調方式 | 0.3
2.3 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 |  | 2.3 | 空調方式 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.3 | Q1 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | Q1 2 | 空調方式（既存） | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 2.3 | Q1 2 | 空調方式 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.3 | Q1 2 | [15 empty] | 2.3 | Q1 2 | [14 empty] | 2.3 | Q1 2 |  | 0
2.3.1 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 1 | 上下温度差 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.3.1 | Q1 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3.1 | Q1 2.3 | 上下温度差 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 2.3.1 | Q1 2.3 | 上下温度差 | [13 empty] | 2.3.1 | Q1 2.3 | [5 empty] | 0 | [9 empty] | 2.3.1 | Q1 2.3 | [14 empty] | 2.3.1 | Q1 2.3 |  | 0
2.3.2 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 2 | 平均気流速度 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.3.2 | Q1 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3.2 | Q1 2.3 | 平均気流速度 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 2.3.2 | Q1 2.3 | 平均気流速度 | [13 empty] | 2.3.2 | Q1 2.3 | [5 empty] | 0 | [9 empty] | 2.3.2 | Q1 2.3 | [14 empty] | 2.3.2 | Q1 2.3 |  | 0
3 | 光・視環境 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.25 | 0 | 3 | 光・視環境 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3 | Q1 | 光・視環境 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 3 | Q1 | 光・視環境 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 3 | Q1 | 光・視環境 | 0.25 | 0.25 | 0.25 | 0.25 |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 3 | Q1 | 光・視環境 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  |  | 3 | Q1 | 光・視環境 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 3 | Q1 | 光・視環境 | 0.25 | bar: 事務所 to ホテル
3.1 | 昼光利用 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.3 | 0 |  | 3.1 | 昼光利用 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.1 | Q1 3 | 昼光利用 | 0.3 | 0.3 | 0.5 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 3.1 | Q1 3 | 昼光利用 | 0.3 | 0.3 | 0.5 | 1 |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 3.1 | Q1 3 | 昼光利用 | 0.3 | 0.3 | 0.5 | 1 |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 3.1 | Q1 3 | 昼光利用 | 0.3 | 0.3 | 0.5 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  | 3.1 | Q1 3 | 昼光利用 | 0.3 | 0.3 | 0.5 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 3.1 | Q1 3 | 昼光利用 | 0.3 | bar: 事務所 to ホテル
3.1.1 | 昼光率 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.6 | 0 |  |  | 1 | 昼光率 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.1.1 | Q1 3.1 | 昼光率 | 0.6 | 0.6 | 0 | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 3.1.1 | Q1 3.1 | 昼光率 | 0.6 | 0.6 |  |  |  | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 3.1.1 | Q1 3.1 | 昼光率 | 0.6 | 0.6 |  |  |  | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 3.1.1 | Q1 3.1 | 昼光率 | 0.6 | 0.6 |  |  | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 |  | 3.1.1 | Q1 3.1 | 昼光率 | 0.6 | 0.6 | 0 | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 3.1.1 | Q1 3.1 | 昼光率 | 0.6
3.1.2 | 方位別開口 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 2 | 方位別開口 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.1.2 | Q1 3.1 | 方位別開口 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 3.1.2 | Q1 3.1 | 方位別開口 | [12 empty] | 0.3 | 3.1.2 | Q1 3.1 | 方位別開口 | [12 empty] | 0.3 | 3.1.2 | Q1 3.1 | 方位別開口 | [12 empty] | 0.3 |  | 3.1.2 | Q1 3.1 | 方位別開口 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 3.1.2 | Q1 3.1 | 方位別開口 | 0
3.1.3 | 昼光利用設備 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.4 | 0 |  |  | 3 | 昼光利用設備 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [10 empty] | 4 |  |  |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.1.3 | Q1 3.1 | 昼光利用設備 | 0.4 | 0.4 | 1 | 1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 3.1.3 | Q1 3.1 | 昼光利用設備 | 0.4 | 0.4 | 1 | 1 |  | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 3.1.3 | Q1 3.1 | 昼光利用設備 | 0.4 | 0.4 | 1 | 1 |  | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 3.1.3 | Q1 3.1 | 昼光利用設備 | 0.4 | 0.4 | 1 | 1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 |  | 3.1.3 | Q1 3.1 | 昼光利用設備 | 0.4 | 0.4 | 1 | 1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 3.1.3 | Q1 3.1 | 昼光利用設備 | 0.4
3.2 | グレア対策 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.3 | 0 |  | 3.2 | グレア対策 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.2 | Q1 3 | グレア対策 | 0.3 | 0.3 | 0 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 3.2 | Q1 3 | グレア対策 | 0.3 | 0.3 |  |  |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 3.2 | Q1 3 | グレア対策 | 0.3 | 0.3 |  |  |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 3.2 | Q1 3 | グレア対策 | 0.3 | 0.3 |  |  |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  | 3.2 | Q1 3 | グレア対策 | 0.3 | 0.3 | 0 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 3.2 | Q1 3 | グレア対策 | 0.3 | bar: 事務所 to ホテル
3.2.1 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 1 | 照明器具のグレア |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.2.1 | Q1 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2.1 | Q1 3.2 | 照明器具のグレア | 0.4 | 0.4 |  |  |  | 0.4 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 3.2.1 | Q1 3.2 | 照明器具のグレア | [13 empty] | 3.2.1 | Q1 3.2 | [15 empty] | 3.2.1 | Q1 3.2 | 照明器具のグレア | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2.1 | Q1 3.2 | 照明器具のグレア | 0 | bar: 事務所 to ホテル
3.2.2 | 昼光制御 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 1 | 0 |  |  | 1 | 昼光制御 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.2.2 | Q1 3.2 | 昼光制御 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.2.2 | Q1 3.2 | 昼光制御 | 0.6 | 0.6 |  |  |  | 0.6 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 3.2.2 | Q1 3.2 | 昼光制御 | 1 | 1 |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.2.2 | Q1 3.2 | 昼光制御 | 1 | 1 |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 3.2.2 | Q1 3.2 | 昼光制御 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.2.2 | Q1 3.2 | 昼光制御 | 1
3.2.3 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 2 | 映り込み対策 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.2.3 | Q1 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2.3 | Q1 3.3 | 映り込み対策 | [6 empty] | 0.3 | [6 empty] | 3.2.3 | Q1 3.3 | 映り込み対策 | [13 empty] | 3.2.3 | Q1 3.3 | [15 empty] | 3.2.3 | Q1 3.3 | bar: 事務所 to ホテル
3.3 | 照度 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.15 | 0 |  | 3.3 | 照度 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.3 | Q1 3 | 照度 | 0.15 | 0.15 | 0 | 0 | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 3.3 | Q1 3 | 照度 | 0.15 | 0.15 |  |  |  | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 3.3 | Q1 3 | 照度 | 0.15 | 0.15 |  |  |  | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 3.3 | Q1 3 | 照度 | 0.15 | 0.15 |  |  | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 |  | 3.3 | Q1 3 | 照度 | 0.15 | 0.15 | 0 | 0 | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 3.3 | Q1 3 | 照度 | 0.15
3.3.1 | 照度 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 1 | 照度 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.3.1 | Q1 3.3 | 照度 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3.1 | Q1 3.3 | 照度 | [13 empty] | 3.3.1 | Q1 3.3 | 照度 | [13 empty] | 3.3.1 | Q1 3.3 | 照度 |  |  |  |  | 0 | [9 empty] | 3.3.1 | Q1 3.3 | 照度 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3.1 | Q1 3.3 | 照度 | 0
3.3.2 | 照度均斉度 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 2 | 照度均斉度 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.3.2 | Q1 3.3 | 照度均斉度 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3.2 | Q1 3.3 | 照度均斉度 | [13 empty] | 3.3.2 | Q1 3.3 | 照度均斉度 | [13 empty] | 3.3.2 | Q1 3.3 | 照度均斉度 |  |  |  |  | 0 | [9 empty] | 3.3.2 | Q1 3.3 | 照度均斉度 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3.2 | Q1 3.3 | 照度均斉度 | 0
3.4 | 照明制御 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.25 | 0 |  | 3.4 | 照明制御 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.4 | Q1 3 | 照明制御 | 0.25 | 0.25 | 0.5 | 0 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 3.4 | Q1 3 | 照明制御 | 0.25 | 0.25 | 0.5 |  |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 3.4 | Q1 3 | 照明制御 | 0.25 | 0.25 | 0.5 | 0 |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 3.4 | Q1 3 | 照明制御 | 0.25 | 0.25 | 0.5 |  | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  | 3.4 | Q1 3 | 照明制御 | 0.25 | 0.25 | 0.5 | 0 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 3.4 | Q1 3 | 照明制御 | 0.25
4 | 空気質環境 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.25 | 0 | 4 | 空気質環境 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 4 | Q1 | 空気質環境 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 4 | Q1 | 空気質環境 | 0.25 | 0.25 | 0.25 | 0.25 | 0.33 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 4 | Q1 | 空気質環境 | 0.25 | 0.25 | 0.25 | 0.25 | 0.33 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 4 | Q1 | 空気質環境 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  |  | 4 | Q1 | 空気質環境 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 4 | Q1 | 空気質環境 | 0.25 | bar: 事務所 to ホテル
4.1 | 発生源対策 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.5 | 0 |  | 4.1 | 発生源対策 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 4.1 | Q1 4 | 発生源対策 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 0.625 | 0.625 | 0.625 | 4.1 | Q1 4 | 発生源対策 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 0.625 | 0.625 | 0.625 | 4.1 | Q1 4 | 発生源対策 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 0.625 | 0.625 | 0.625 | 4.1 | Q1 4 | 発生源対策 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 0.625 | 0.625 | 0.625 |  | 4.1 | Q1 4 | 発生源対策 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 0.625 | 0.625 | 0.625 | 4.1 | Q1 4 | 発生源対策 | 0.5 | bar: 事務所 to ホテル
4.1.1 | 化学汚染物質 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 1 | 0 |  |  | 1 | 化学汚染物質 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 4.1.1 | Q1 4.1 | 化学汚染物質 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4.1.1 | Q1 4.1 | 化学汚染物質 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.33 | 0.33 | 0.25 | 0.25 | 0.25 | 4.1.1 | Q1 4.1 | 化学汚染物質 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4.1.1 | Q1 4.1 | 化学汚染物質 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 4.1.1 | Q1 4.1 | 化学汚染物質 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4.1.1 | Q1 4.1 | 化学汚染物質 | 1
4.1.2 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 2 | アスベスト対策 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 4.1.2 | Q1 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1.2 | Q1 4.1 | アスベスト対策 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.33 | 0.33 | 0.25 | 0.25 | 0.25 | 4.1.2 | Q1 4.1 | アスベスト対策 | [13 empty] | 4.1.2 | Q1 4.1 | [15 empty] | 4.1.2 | Q1 4.1 | bar: 事務所 to ホテル
4.1.3 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 3 | ダニ・カビ等 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 4.1.3 | Q1 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1.3 | Q1 4.1 |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.33 | 0.33 | 0.25 | 0.25 | 0.25 | 4.1.3 | Q1 4.1 | ダニ・カビ等 | [13 empty] | 4.1.3 | Q1 4.1 | [15 empty] | 4.1.3 | Q1 4.1 | ダニ・カビ等 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1.3 | Q1 4.1 | ダニ・カビ等 | 0
4.1.4 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 4 | レジオネラ対策 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 4.1.4 | Q1 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1.4 | Q1 4.1 | レジオネラ対策 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  | 0.25 | 0.25 | 0.25 | 4.1.4 | Q1 4.1 | レジオネラ対策 | [13 empty] | 4.1.4 | Q1 4.1 | [15 empty] | 4.1.4 | Q1 4.1 | レジオネラ対策 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1.4 | Q1 4.1 | レジオネラ対策 | 0
4.2 | 換気 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.3 | 0 |  | 4.2 | 換気 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 4.2 | Q1 4 | 換気 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.375 | 0.375 | 0.375 | 4.2 | Q1 4 | 換気 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.375 | 0.375 | 0.375 | 4.2 | Q1 4 | 換気 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.375 | 0.375 | 0.375 | 4.2 | Q1 4 | 換気 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.375 | 0.375 | 0.375 |  | 4.2 | Q1 4 | 換気 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.375 | 0.375 | 0.375 | 4.2 | Q1 4 | 換気 | 0.3 | bar: 事務所 to ホテル
4.2.1 | 換気量 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.33333 | 0 |  |  | 1 | 換気量 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 4.2.1 | Q1 4.2 | 換気量 | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.33333 | 4.2.1 | Q1 4.2 | 換気量 | 0.25 | 0.25 | 0.33333 | 0.33333 | 0.33333 | 0.25 | 0.25 | 0.33333 | 0.33333 |  | 0.25 | 0.25 |  | 4.2.1 | Q1 4.2 | 換気量 | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.33333 | 4.2.1 | Q1 4.2 | 換気量 | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.33333 |  | 4.2.1 | Q1 4.2 | 換気量 | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.33333 | 4.2.1 | Q1 4.2 | 換気量 | 0.33333
4.2.2 | 自然換気性能 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.33333 | 0 |  |  | 2 | 自然換気性能 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 4.2.2 | Q1 4.2 | 自然換気性能 | 0.33333 | 0.33333 | 0 | 0 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 0.33333 | 0.33333 | 0.33333 | 4.2.2 | Q1 4.2 | 自然換気性能 | 0.25 | 0.25 |  |  |  | 0.25 | 0.25 |  |  |  | 0.25 | 0.25 | 0.33 | 4.2.2 | Q1 4.2 | 自然換気性能 | 0.33333 | 0.33333 |  |  |  | 0.33333 | 0.33333 |  |  |  | 0.33333 | 0.33333 | 0.33333 | 4.2.2 | Q1 4.2 | 自然換気性能 | 0.33333 | 0.33333 |  |  | 0.33333 | 0.33333 | 0.33333 |  |  |  | 0.33333 | 0.33333 | 0.33333 |  | 4.2.2 | Q1 4.2 | 自然換気性能 | 0.33333 | 0.33333 | 0 | 0 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 0.33333 | 0.33333 | 0.33333 | 4.2.2 | Q1 4.2 | 自然換気性能 | 0.33333
4.2.3 | 取り入れ外気への配慮 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.33333 | 0 |  |  | 3 | 取り入れ外気への配慮 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 4.2.3 | Q1 4.2 | 取り入れ外気への配慮 | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.33333 | 4.2.3 | Q1 4.2 | 取り入れ外気への配慮 | 0.25 | 0.25 | 0.33333 | 0.33333 | 0.33333 | 0.25 | 0.25 | 0.33333 | 0.33333 | 1 | 0.25 | 0.25 | 0.33 | 4.2.3 | Q1 4.2 | 取り入れ外気への配慮 | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.33333 | 4.2.3 | Q1 4.2 | 取り入れ外気への配慮 | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.33333 |  | 4.2.3 | Q1 4.2 | 取り入れ外気への配慮 | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.33333 | 4.2.3 | Q1 4.2 | 取り入れ外気への配慮 | 0.33333
4.2.4 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 4 | 給気計画 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 4.2.4 | Q1 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2.4 | Q1 4.2 | 給気計画 | 0.25 | 0.25 | 0.33333 | 0.33333 | 0.33333 | 0.25 | 0.25 | 0.33333 | 0.33333 |  | 0.25 | 0.25 | 0.33 | 4.2.4 | Q1 4.2 | 給気計画 | [13 empty] | 4.2.4 | Q1 4.2 | [15 empty] | 4.2.4 | Q1 4.2 | bar: 事務所 to ホテル
4.3 | 運用管理 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.2 | 0 |  | 4.3 | 運用管理 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 4.3 | Q1 4 | 運用管理 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 4.3 | Q1 4 | 運用管理 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 4.3 | Q1 4 | 運用管理 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 4.3 | Q1 4 | 運用管理 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | [5 empty] | 4.3 | Q1 4 | 運用管理 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 4.3 | Q1 4 | 運用管理 | 0.2 | bar: 事務所 to ホテル
4.3.1 | CO2の監視 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.5 | 0 |  |  | 1 | CO2の監視 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 4.3.1 | Q1 4.3 | CO2の監視 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3.1 | Q1 4.3 | CO2の監視 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [6 empty] | 4.3.1 | Q1 4.3 | CO2の監視 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [6 empty] | 4.3.1 | Q1 4.3 | CO2の監視 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [7 empty] | 4.3.1 | Q1 4.3 | CO2の監視 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3.1 | Q1 4.3 | CO2の監視 | 0.5
4.3.2 | 喫煙の制御 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.5 | 0 |  |  | 2 | 喫煙の制御 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 4.3.2 | Q1 4.3 | 喫煙の制御 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 0 | 0 | 0 | 0 | 4.3.2 | Q1 4.3 | 喫煙の制御 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 |  |  |  |  | 4.3.2 | Q1 4.3 | 喫煙の制御 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 |  |  |  |  | 4.3.2 | Q1 4.3 | 喫煙の制御 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | [5 empty] | 4.3.2 | Q1 4.3 | 喫煙の制御 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 0 | 0 | 0 | 0 | 4.3.2 | Q1 4.3 | 喫煙の制御 | 0.5
Q2 | サービス性能 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.3 | 0 | Q2 | サービス性能 |  |  |  | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 小中高 | 病院 | ホテル | 集合住宅 | 病院o | ホテルo | 集合住宅o | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Q2 | Q | サービス性能 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | Q2 | Q | サービス性能 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | Q2 | Q | サービス性能 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | Q2 | Q | サービス性能 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | Q2 | Q | サービス性能 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | Q2 | Q | サービス性能 | 0.4
1 | 機能性 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.4 | 0 | 1 | 機能性 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1 | Q2 | 機能性 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 1 | Q2 | 機能性 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | 1 | Q2 | 機能性 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | 1 | Q2 | 機能性 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  |  | 1 | Q2 | 機能性 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0 | 0 | 0 | 1 | Q2 | 機能性 | 0.6 | bar: 事務所 to ホテル
1.1 | 機能性・使いやすさ | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.4 | 0 |  | 1.1 | 機能性・使いやすさ |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.1 | Q2 1 | 機能性・使いやすさ | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 1.1 | Q2 1 | 機能性・使いやすさ | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 1.1 | Q2 1 | 機能性・使いやすさ | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 1.1 | Q2 1 | 機能性・使いやすさ | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 |  | 1.1 | Q2 1 | 機能性・使いやすさ | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 1.1 | Q2 1 | 機能性・使いやすさ | 0.4 | bar: 事務所 to ホテル
1.1.1 | 広さ・収納性 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.33333 | 0 |  |  | 1 | 広さ・収納性 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.1.1 | Q2 1.1 | 広さ・収納性 | 0.33333 | 0 | 0 | 0 | 0 | 0.33333 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0 | 1.1.1 | Q2 1.1 | 広さ・収納性 | 0.33333 |  |  |  |  | 0.33333 | 0.5 |  |  |  | 1 | 0.5 |  | 1.1.1 | Q2 1.1 | 広さ・収納性 | 0.33333 |  |  |  |  | 0.33333 | 0.5 |  |  |  | 1 | 0.5 |  | 1.1.1 | Q2 1.1 | 広さ・収納性 | 0.33333 |  |  |  |  | 0.33333 |  |  |  |  | 1 | 0.5 |  |  | 1.1.1 | Q2 1.1 | 広さ・収納性 | 0.33333 | 0 | 0 | 0 | 0 | 0.33333 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0 | 1.1.1 | Q2 1.1 | 広さ・収納性 | 0.33333
1.1.2 | 高度情報通信設備対応 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.33333 | 0 |  |  | 2 | 高度情報通信設備対応 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.1.2 | Q2 1.1 | 高度情報通信設備対応 | 0.33333 | 0 | 0 | 0 | 0 | 0.33333 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1.1.2 | Q2 1.1 | 高度情報通信設備対応 | 0.33333 |  |  |  |  | 0.33333 | [5 empty] | 0.5 | 1 | 1.1.2 | Q2 1.1 | 高度情報通信設備対応 | 0.33333 |  |  |  |  | 0.33333 | [5 empty] | 0.5 | 1 | 1.1.2 | Q2 1.1 | 高度情報通信設備対応 | 0.33333 |  |  |  |  | 0.33333 | [5 empty] | 0.5 | 1 |  | 1.1.2 | Q2 1.1 | 高度情報通信設備対応 | 0.33333 | 0 | 0 | 0 | 0 | 0.33333 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1.1.2 | Q2 1.1 | 高度情報通信設備対応 | 0.33333
1.1.3 | バリアフリー計画 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.33333 | 0 |  |  | 3 | バリアフリー計画 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.1.3 | Q2 1.1 | バリアフリー計画 | 0.33333 | 1 | 1 | 1 | 1 | 0.33333 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1.1.3 | Q2 1.1 | バリアフリー計画 | 0.33333 | 1 | 1 | 1 | 1 | 0.33333 | 0.5 | 1 | 1 | 1 |  |  |  | 1.1.3 | Q2 1.1 | バリアフリー計画 | 0.33333 | 1 | 1 | 1 | 1 | 0.33333 | 0.5 | 1 | 1 | 1 |  |  |  | 1.1.3 | Q2 1.1 | バリアフリー計画 | 0.33333 | 1 | 1 | 1 | 1 | 0.33333 | 1 | 1 | 1 | 1 |  |  |  |  | 1.1.3 | Q2 1.1 | バリアフリー計画 | 0.33333 | 1 | 1 | 1 | 1 | 0.33333 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1.1.3 | Q2 1.1 | バリアフリー計画 | 0.33333
1.2 | 心理性・快適性 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.3 | 0 |  | 1.2 | 心理性・快適性 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.2 | Q2 1 | 心理性・快適性 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 1.2 | Q2 1 | 心理性・快適性 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 1.2 | Q2 1 | 心理性・快適性 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 1.2 | Q2 1 | 心理性・快適性 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 |  | 1.2 | Q2 1 | 心理性・快適性 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 1.2 | Q2 1 | 心理性・快適性 | 0.45 | bar: 事務所 to ホテル
1.2.1 | 広さ感・景観 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.33333 | 0 |  |  | 1 | 広さ感・景観 | （天井高） | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.2.1 | Q2 1.2 | 広さ感・景観 | 0.33333 | 0.5 | 0.33333 | 0.5 | 0 | 0.33333 | 0.5 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 1.2.1 | Q2 1.2 | 広さ感・景観 | 0.33333 | [12 empty] | 1.2.1 | Q2 1.2 | 広さ感・景観 | 0.33333 | 0.5 | 0.33333 | 0.5 |  | 0.33333 | 0.5 |  |  |  | 0.5 | 0.5 | 0.5 | 1.2.1 | Q2 1.2 | 広さ感・景観 | 0.33333 | 0.5 | 0.33333 | 0.5 |  | 0.33333 | 0.5 |  |  |  | 0.5 | 0.5 | 0.5 |  | 1.2.1 | Q2 1.2 | 広さ感・景観 | 0.33333 | 0.5 | 0.33333 | 0.5 | 0 | 0.33333 | 0.5 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 1.2.1 | Q2 1.2 | 広さ感・景観（天井高） | 0.15
| 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 2 | 広さ感・景観 | （窓の配置） | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [65 empty] | 1.2.2 | Q2 1.2 | 広さ感・景観（窓） | 0.15
1.2.2 | リフレッシュスペース | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.33333 | 0 |  |  | 2 | リフレッシュスペース |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.2.2 | Q2 1.2 | リフレッシュスペース | 0.33333 | 0 | 0.33333 | 0 | 0 | 0.33333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2.2 | Q2 1.2 | リフレッシュスペース | 0.33333 |  | 0.5 | [10 empty] | 1.2.2 | Q2 1.2 | リフレッシュスペース | 0.33333 | 0 | 0.33333 |  |  | 0.33333 | 0 | [6 empty] | 1.2.2 | Q2 1.2 | リフレッシュスペース | 0.33333 |  | 0.33333 |  |  | 0.33333 | [8 empty] | 1.2.2 | Q2 1.2 | リフレッシュスペース | 0.33333 | 0 | 0.33333 | 0 | 0 | 0.33333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2.3 | Q2 1.2 | リフレッシュスペース | 0.25
1.2.3 | 内装計画 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.33333 | 0 |  |  | 3 | 内装計画 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.2.3 | Q2 1.2 | 内装計画 | 0.33333 | 0.5 | 0.33333 | 0.5 | 1 | 0.33333 | 0.5 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 1.2.3 | Q2 1.2 | 内装計画 | 0.33333 | 1 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.2.3 | Q2 1.2 | 内装計画 | 0.33333 | 0.5 | 0.33333 | 0.5 | 1 | 0.33333 | 0.5 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 1.2.3 | Q2 1.2 | 内装計画 | 0.33333 | 0.5 | 0.33333 | 0.5 | 1 | 0.33333 | 0.5 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 |  | 1.2.3 | Q2 1.2 | 内装計画 | 0.33333 | 0.5 | 0.33333 | 0.5 | 1 | 0.33333 | 0.5 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 1.2.4 | Q2 1.2 | 内装計画 | 0.25
| 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 5 | 知的生産性向上の取組み |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [65 empty] | 1.2.5 | Q2 1.2 | 知的生産性向上の取組み | 0.2
1.3 | 維持管理 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.3 | 0 |  | 1.3 | 維持管理 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.3 | Q2 1 | 維持管理 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 1.3 | Q2 1 | 維持管理 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 1.3 | Q2 1 | 維持管理 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 1.3 | Q2 1 | 維持管理 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | 1.3 | Q2 1 | 維持管理 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 1.3 | Q2 1 | 維持管理 | 0.15 | bar: 事務所 to ホテル
1.3.1 | 維持管理に配慮した設計 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.5 | 0 |  |  | 1 | 維持管理に配慮した設計 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.3.1 | Q2 1.3 | 維持管理に配慮した設計 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 1.3.1 | Q2 1.3 | 総合的な取組み | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 1.3.1 | Q2 1.3 | 維持管理に配慮した設計 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 1.3.1 | Q2 1.3 | 維持管理に配慮した設計 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | 1.3.1 | Q2 1.3 | 維持管理に配慮した設計 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 1.3.1 | Q2 1.3 | 維持管理に配慮した設計 | 1
1.3.2 | 維持管理用機能の確保 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.5 | 0 |  |  | 2 | 維持管理用機能の確保 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.3.2 | Q2 1.3 | 維持管理用機能の確保 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 1.3.2 | Q2 1.3 | 清掃管理業務 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 1.3.2 | Q2 1.3 | 維持管理用機能の確保 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 1.3.2 | Q2 1.3 | 維持管理用機能の確保 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | 1.3.2 | Q2 1.3 | 維持管理用機能の確保 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 1.3.2 | Q2 1.3 | 維持管理用機能の確保 | 0
0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 3 | 衛生管理業務 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3.3 | Q2 1.3 | 衛生管理業務 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0 | 0 | [15 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | bar: 事務所 to ホテル
2 | 耐用性・信頼性 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.3 | 0 | 2 | 耐用性・信頼性 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2 | Q2 | 耐用性・信頼性 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 2 | Q2 | 耐用性・信頼性 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 2 | Q2 | 耐用性・信頼性 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 2 | Q2 | 耐用性・信頼性 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | 2 | Q2 | 耐用性・信頼性 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2 | Q2 | 耐用性・信頼性 | 0.2 | bar: 事務所 to ホテル
2.1 | 耐震･免震・制震・制振 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.5 | 0 |  | 2.1 | 耐震･免震・制震・制振 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.1 | Q2 2 | 耐震･免震・制震・制振 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 2.1 | Q2 2 | 耐震･免震 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.1 | Q2 2 | 耐震･免震 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 2.1 | Q2 2 | 耐震･免震・制震・制振 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | 2.1 | Q2 2 | 耐震･免震・制震・制振 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 2.1 | Q2 2 | 耐震･免震・制震・制振 | 0.4 | bar: 事務所 to ホテル
2.1.1 | 耐震性 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.8 | 0 |  |  | 1 | 耐震性(建物のこわれにくさ) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.1.1 | Q2 2.1 | 耐震性 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0 | 0 | 0 | 2.1.1 | Q2 2.1 | 耐震性 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0 | 0 | 0 | 2.1.1 | Q2 2.1 | 耐震性 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  |  |  | 2.1.1 | Q2 2.1 | 耐震性 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  |  |  |  | 2.1.1 | Q2 2.1 | 耐震性 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 2.1.1 | Q2 2.1 | 耐震性 | 0.8
2.1.2 | 免震・制震・制振性能 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.2 | 0 |  |  | 2 | 免震・制震・制振性能 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.1.2 | Q2 2.1 | 免震・制震・制振性能 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.1.2 | Q2 2.1 | 免震・制振性能 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.1.2 | Q2 2.1 | 免震・制振性能 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.1.2 | Q2 2.1 | 免震・制震・制振性能 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.1.2 | Q2 2.1 | 免震・制震・制振性能 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1.2 | Q2 2.1 | 免震・制震・制振性能 | 0.2
2.2 | 部品・部材の耐用年数 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.3 | 0 |  | 2.2 | 部品・部材の耐用年数 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.2 | Q2 2 | 部品・部材の耐用年数 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 2.2 | Q2 2 | 部品・部材の耐用年数 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.2 | Q2 2 | 部品・部材の耐用年数 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 2.2 | Q2 2 | 部品・部材の耐用年数 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | 2.2 | Q2 2 | 部品・部材の耐用年数 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | Q2 2 | 部品・部材の耐用年数 | 0 | bar: 事務所 to ホテル
2.2.1 | 躯体材料の耐用年数 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.2 | 0 |  |  | 1 | 躯体材料の耐用年数 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.2.1 | Q2 2.2 | 躯体材料の耐用年数 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.2.1 | Q2 2.2 | 躯体材料の耐用年数 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.2.1 | Q2 2.2 | 躯体材料の耐用年数 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.2.1 | Q2 2.2 | 躯体材料の耐用年数 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.2.1 | Q2 2.2 | 躯体材料の耐用年数 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2.1 | Q2 2.2 | 躯体材料の耐用年数 | 0
2.2.2 | 外壁仕上げ材の補修必要間隔 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.2 | 0 |  |  | 2 | 外壁仕上げ材の補修必要間隔 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.2.2 | Q2 2.2 | 外壁仕上げ材の補修必要間隔 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.2.2 | Q2 2.2 | 外壁仕上げ材の補修必要間隔 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.2.2 | Q2 2.2 | 外壁仕上げ材の補修必要間隔 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.2.2 | Q2 2.2 | 外壁仕上げ材の補修必要間隔 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.2.2 | Q2 2.2 | 外壁仕上げ材の補修必要間隔 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2.2 | Q2 2.2 | 外壁仕上げ材の補修必要間隔 | 0
2.2.3 | 主要内装仕上げ材の更新必要間隔 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.1 | 0 |  |  | 3 | 主要内装仕上げ材の更新必要間隔 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.2.3 | Q2 2.2 | 主要内装仕上げ材の更新必要間隔 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 2.2.3 | Q2 2.2 | 主要内装仕上げ材の更新必要間隔 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2.3 | Q2 2.2 | 主要内装仕上げ材の更新必要間隔 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 2.2.3 | Q2 2.2 | 主要内装仕上げ材の更新必要間隔 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  |  | 2.2.3 | Q2 2.2 | 主要内装仕上げ材の更新必要間隔 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2.3 | Q2 2.2 | 主要内装仕上げ材の更新必要間隔 | 0
2.2.4 | 空調換気ダクトの更新必要間隔 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.1 | 0 |  |  | 4 | 空調換気ダクトの更新必要間隔 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.2.4 | Q2 2.2 | 空調換気ダクトの更新必要間隔 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 2.2.4 | Q2 2.2 | 空調換気ダクトの更新必要間隔 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 2.2.4 | Q2 2.2 | 空調換気ダクトの更新必要間隔 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 2.2.4 | Q2 2.2 | 空調換気ダクトの更新必要間隔 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  |  | 2.2.4 | Q2 2.2 | 空調換気ダクトの更新必要間隔 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2.4 | Q2 2.2 | 空調換気ダクトの更新必要間隔 | 0
2.2.5 | 空調・給排水配管の更新必要間隔 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.2 | 0 |  |  | 5 | 空調・給排水配管の更新必要間隔 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.2.5 | Q2 2.2 | 空調・給排水配管の更新必要間隔 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.2.5 | Q2 2.2 | 空調・給排水配管の更新必要間隔 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 2.2.5 | Q2 2.2 | 空調・給排水配管の更新必要間隔 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.2.5 | Q2 2.2 | 空調・給排水配管の更新必要間隔 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.2.5 | Q2 2.2 | 空調・給排水配管の更新必要間隔 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2.5 | Q2 2.2 | 空調・給排水配管の更新必要間隔 | 0
2.2.6 | 主要設備機器の更新必要間隔 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.2 | 0 |  |  | 6 | 主要設備機器の更新必要間隔 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.2.6 | Q2 2.2 | 主要設備機器の更新必要間隔 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.2.6 | Q2 2.2 | 主要設備機器の更新必要間隔 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.2.6 | Q2 2.2 | 主要設備機器の更新必要間隔 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.2.6 | Q2 2.2 | 主要設備機器の更新必要間隔 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.2.6 | Q2 2.2 | 主要設備機器の更新必要間隔 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2.6 | Q2 2.2 | 主要設備機器の更新必要間隔 | 0
2.3 | 適切な更新 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 |  | 2.3 | 適切な更新 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.3 | Q2 2 | 適切な更新 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | Q2 2 | 適切な更新 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3 | Q2 2 | 適切な更新 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2.3 | Q2 2 | 適切な更新 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2.3 | Q2 2 | 適切な更新 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | Q2 2 | 適切な更新 | 0 | bar: 事務所 to ホテル
2.3.1 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 1 | 屋上（屋根）・外壁仕上げ材の更新 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.3.1 | Q2 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3.1 | Q2 2.3 | 屋上（屋根）・外壁仕上げ材の更新 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 2.3.1 | Q2 2.3 | 屋上（屋根）・外壁仕上げ材の更新 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2.3.1 | Q2 2.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2.3.1 | Q2 2.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3.1 | Q2 2.3 | 屋上（屋根）・外壁仕上げ材の更新 | 0
2.3.2 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 2 | 配管・配線材の更新 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.3.2 | Q2 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3.2 | Q2 2.3 | 配管・配線材の更新 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 2.3.2 | Q2 2.3 | 配管・配線材の更新 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2.3.2 | Q2 2.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2.3.2 | Q2 2.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3.2 | Q2 2.3 | 配管・配線材の更新 | 0
2.3.3 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 3 | 主用設備機器の更新 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.3.3 | Q2 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3.3 | Q2 2.3 | 主要設備機器の更新 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 2.3.3 | Q2 2.3 | 主要設備機器の更新 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2.3.3 | Q2 2.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2.3.3 | Q2 2.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3.3 | Q2 2.3 | 主要設備機器の更新 | 0
2.4 | 信頼性 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.2 | 0 |  | 2.4 | 信頼性 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.4 | Q2 2 | 信頼性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4 | Q2 2 | 信頼性 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.4 | Q2 2 | 信頼性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.4 | Q2 2 | 信頼性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.4 | Q2 2 | 信頼性 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 2.4 | Q2 2 | 信頼性 | 0.6 | bar: 事務所 to ホテル
2.4.1 | 空調・換気設備 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.2 | 0 |  |  | 1 | 空調・換気設備 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.4.1 | Q2 2.4 | 空調・換気設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.1 | Q2 2.4 | 空調・換気設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.1 | Q2 2.4 | 空調・換気設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.4.1 | Q2 2.4 | 空調・換気設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.4.1 | Q2 2.4 | 空調・換気設備 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4.1 | Q2 2.4 | 空調・換気設備 | 0.15
2.4.2 | 給排水・衛生設備 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.2 | 0 |  |  | 2 | 給排水・衛生設備 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.4.2 | Q2 2.4 | 給排水・衛生設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.2 | Q2 2.4 | 給排水・衛生設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.2 | Q2 2.4 | 給排水・衛生設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.4.2 | Q2 2.4 | 給排水・衛生設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.4.2 | Q2 2.4 | 給排水・衛生設備 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4.2 | Q2 2.4 | 給排水・衛生設備 | 0.15
2.4.3 | 電気設備 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.2 | 0 |  |  | 3 | 電気設備 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.4.3 | Q2 2.4 | 電気設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.3 | Q2 2.4 | 電気設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.3 | Q2 2.4 | 電気設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.4.3 | Q2 2.4 | 電気設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.4.3 | Q2 2.4 | 電気設備 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4.3 | Q2 2.4 | 電気設備 | 0.25
2.4.4 | 機械・配管支持方法 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.2 | 0 |  |  | 4 | 機械・配管支持方法 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.4.4 | Q2 2.4 | 機械・配管支持方法 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.4 | Q2 2.4 | 機械・配管支持方法 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.4 | Q2 2.4 | 機械・配管支持方法 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.4.4 | Q2 2.4 | 機械・配管支持方法 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.4.4 | Q2 2.4 | 機械・配管支持方法 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 2.4.4 | Q2 2.4 | 機械・配管支持方法 | 0.2
2.4.5 | 通信・情報設備 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.2 | 0 |  |  | 5 | 通信・情報設備 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.4.5 | Q2 2.4 | 通信・情報設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.5 | Q2 2.4 | 通信・情報設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.5 | Q2 2.4 | 通信・情報設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.4.5 | Q2 2.4 | 通信・情報設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.4.5 | Q2 2.4 | 通信・情報設備 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4.5 | Q2 2.4 | 通信・情報設備 | 0.25
0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | Q | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Q |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Q | [15 empty] | Q | [16 empty] | Q |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Q |  | 0
3 | 対応性・更新性 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.3 | 0 | 3 | 対応性・更新性 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3 | Q2 | 対応性・更新性 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 3 | Q2 | 対応性・更新性 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 3 | Q2 | 対応性・更新性 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 3 | Q2 | 対応性・更新性 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | 3 | Q2 | 対応性・更新性 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | Q2 | 対応性・更新性 | 0.2 | bar: 事務所 to ホテル
3.1 | 空間のゆとり | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.3 | 0 |  | 3.1 | 空間のゆとり |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.1 | Q2 3 | 空間のゆとり | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0.5 | 0.5 | 0.5 | 3.1 | Q2 3 | 空間のゆとり | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  | 0.5 | 0.5 | 0.5 | 3.1 | Q2 3 | 空間のゆとり | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  | 0.5 | 0.5 | 0.5 | 3.1 | Q2 3 | 空間のゆとり | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  | 0.5 | 0.5 | 0.5 |  | 3.1 | Q2 3 | 空間のゆとり | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | Q2 3 | 空間のゆとり | 0.3 | bar: 事務所 to ホテル
3.1.1 | 階高のゆとり | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.6 | 0 |  |  | 1 | 階高のゆとり |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.1.1 | Q2 3.1 | 階高のゆとり | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0.6 | 0.6 | 0.6 | 0 | 0 | 0.6 | 0.6 | 0.6 | 3.1.1 | Q2 3.1 | 階高のゆとり | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0.6 | 0.6 | 0.6 |  |  | 0.6 | 0.6 | 0.6 | 3.1.1 | Q2 3.1 | 階高のゆとり | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0.6 | 0.6 | 0.6 |  |  | 0.6 | 0.6 | 0.6 | 3.1.1 | Q2 3.1 | 階高のゆとり | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0.6 | 0.6 | 0.6 |  |  | 0.6 | 0.6 | 0.6 |  | 3.1.1 | Q2 3.1 | 階高のゆとり | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1.1 | Q2 3.1 | 階高のゆとり | 0
3.1.2 | 空間の形状・自由さ | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.4 | 0 |  |  | 2 | 空間の形状・自由さ |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.1.2 | Q2 3.1 | 空間の形状・自由さ | 0.4 | 0.4 | 0.4 | 0.4 | 1 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0.4 | 0.4 | 0.4 | 3.1.2 | Q2 3.1 | 空間の形状・自由さ | 0.4 | 0.4 | 0.4 | 0.4 | 1 | 0.4 | 0.4 | 0.4 |  |  | 0.4 | 0.4 | 0.4 | 3.1.2 | Q2 3.1 | 空間の形状・自由さ | 0.4 | 0.4 | 0.4 | 0.4 | 1 | 0.4 | 0.4 | 0.4 |  |  | 0.4 | 0.4 | 0.4 | 3.1.2 | Q2 3.1 | 空間の形状・自由さ | 0.4 | 0.4 | 0.4 | 0.4 | 1 | 0.4 | 0.4 | 0.4 |  |  | 0.4 | 0.4 | 0.4 |  | 3.1.2 | Q2 3.1 | 空間の形状・自由さ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1.2 | Q2 3.1 | 空間の形状・自由さ | 1
3.2 | 荷重のゆとり | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.3 | 0 |  | 3.2 | 荷重のゆとり |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.2 | Q2 3 | 荷重のゆとり | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0.5 | 0.5 | 0.5 | 3.2 | Q2 3 | 荷重のゆとり | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  | 0.5 | 0.5 | 0.5 | 3.2 | Q2 3 | 荷重のゆとり | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  | 0.5 | 0.5 | 0.5 | 3.2 | Q2 3 | 荷重のゆとり | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  | 0.5 | 0.5 | 0.5 |  | 3.2 | Q2 3 | 荷重のゆとり | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | Q2 3 | 荷重のゆとり | 0.3
3.3 | 設備の更新性 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.4 | 0 |  | 3.3 | 設備の更新性 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.3 | Q2 3 | 設備の更新性 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1 | 1 | 0 | 0 | 0 | 3.3 | Q2 3 | 設備の更新性 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1 | 1 |  |  |  | 3.3 | Q2 3 | 設備の更新性 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1 | 1 |  |  |  | 3.3 | Q2 3 | 設備の更新性 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1 | 1 |  |  |  |  | 3.3 | Q2 3 | 設備の更新性 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | Q2 3 | 設備の更新性 | 0.4 | bar: 事務所 to ホテル
3.3.1 | 空調配管の更新性 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.2 | 0 |  |  | 1 | 空調配管の更新性 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.3.1 | Q2 3.3 | 空調配管の更新性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 3.3.1 | Q2 3.3 | 空調配管の更新性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3.1 | Q2 3.3 | 空調配管の更新性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3.1 | Q2 3.3 | 空調配管の更新性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 3.3.1 | Q2 3.3 | 空調配管の更新性 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3.1 | Q2 3.3 | 空調配管の更新性 | 0
3.3.2 | 給排水管の更新性 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.2 | 0 |  |  | 2 | 給排水管の更新性 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.3.2 | Q2 3.3 | 給排水管の更新性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 3.3.2 | Q2 3.3 | 給排水管の更新性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3.2 | Q2 3.3 | 給排水管の更新性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3.2 | Q2 3.3 | 給排水管の更新性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 3.3.2 | Q2 3.3 | 給排水管の更新性 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3.2 | Q2 3.3 | 給排水管の更新性 | 0.4
3.3.3 | 電気配線の更新性 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.1 | 0 |  |  | 3 | 電気配線の更新性 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.3.3 | Q2 3.3 | 電気配線の更新性 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 3.3.3 | Q2 3.3 | 電気配線の更新性 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 3.3.3 | Q2 3.3 | 電気配線の更新性 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 3.3.3 | Q2 3.3 | 電気配線の更新性 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  |  | 3.3.3 | Q2 3.3 | 電気配線の更新性 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3.3 | Q2 3.3 | 電気配線の更新性 | 0.1
3.3.4 | 通信配線の更新性 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.1 | 0 |  |  | 4 | 通信配線の更新性 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.3.4 | Q2 3.3 | 通信配線の更新性 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 3.3.4 | Q2 3.3 | 通信配線の更新性 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 3.3.4 | Q2 3.3 | 通信配線の更新性 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 3.3.4 | Q2 3.3 | 通信配線の更新性 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  |  | 3.3.4 | Q2 3.3 | 通信配線の更新性 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3.4 | Q2 3.3 | 通信配線の更新性 | 0.1
3.3.5 | 設備機器の更新性 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.2 | 0 |  |  | 5 | 設備機器の更新性 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.3.5 | Q2 3.3 | 設備機器の更新性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 3.3.5 | Q2 3.3 | 設備機器の更新性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3.5 | Q2 3.3 | 設備機器の更新性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3.5 | Q2 3.3 | 設備機器の更新性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 3.3.5 | Q2 3.3 | 設備機器の更新性 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3.5 | Q2 3.3 | 設備機器の更新性 | 0.2
3.3.6 | バックアップスペースの確保 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.2 | 0 |  |  | 6 | バックアップスペースの確保 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.3.6 | Q2 3.3 | バックアップスペースの確保 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 3.3.6 | Q2 3.3 | バックアップスペースの確保 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3.6 | Q2 3.3 | バックアップスペースの確保 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3.6 | Q2 3.3 | バックアップスペースの確保 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 3.3.6 | Q2 3.3 | バックアップスペースの確保 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3.6 | Q2 3.3 | バックアップスペースの確保 | 0.2
Q3 | 室外環境（敷地内） | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.3 | 0 | Q3 | 室外環境（敷地内） |  |  |  | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 小中高 | 病院 | ホテル | 集合住宅 | 病院o | ホテルo | 集合住宅o | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Q3 | Q | 室外環境（敷地内） | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | Q3 | Q | 室外環境（敷地内） | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | Q3 | Q | 室外環境（敷地内） | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | Q3 | Q | 室外環境（敷地内） | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | Q3 | Q | 室外環境（敷地内） | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | Q3 | Q | 室外環境（敷地内） | 0.1
1 | 生物資源の保全と創出 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.3 | 0 | 1 | 生物環境の保全と創出 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1 | Q3 | 生物資源の保全と創出 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 1 | Q3 | 生物資源の保全と創出 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 1 | Q3 | 生物資源の保全と創出 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 1 | Q3 | 生物資源の保全と創出 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | 1 | Q3 | 生物資源の保全と創出 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 1 | Q3 | 生物資源の保全と創出 | 0
1 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 | 1 | 豊かな室外環境 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [65 empty] | 1 | Q3 | 豊かな室外環境 | 1
1.1 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  | 1.1 | 知的生産性向上の取組み |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [65 empty] | 3.1 | Q3 3 | 知的生産性向上の取組み | 1
2 | まちなみ・景観への配慮 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.4 | 0 | 2 | まちなみ・景観への配慮 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2 | Q3 | まちなみ・景観への配慮 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 2 | Q3 | まちなみ・景観への配慮 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 2 | Q3 | まちなみ・景観への配慮 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | 2 | Q3 | まちなみ・景観への配慮 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  |  | 2 | Q3 | まちなみ・景観への配慮 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 2 | Q3 | まちなみ・景観への配慮 | 0
3 | 地域性・アメニティへの配慮 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.3 | 0 | 3 | 地域性・アメニティへの配慮 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3 | Q3 | 地域性・アメニティへの配慮 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 3 | Q3 | 地域性・アメニティへの配慮 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 3 | Q3 | 地域性・アメニティへの配慮 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 3 | Q3 | 地域性・アメニティへの配慮 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | 3 | Q3 | 地域性・アメニティへの配慮 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 3 | Q3 | 地域性・アメニティへの配慮 | 0 | bar: 事務所 to ホテル
3.1 | 地域性への配慮、快適性の向上 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.5 | 0 |  | 3.1 | 地域性への配慮、快適性の向上 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.1 | Q3 3 | 地域性への配慮、快適性の向上 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 3.1 | Q3 3 | 地域性への配慮、快適性の向上 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 3.1 | Q3 3 | 地域性への配慮、快適性の向上 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 3.1 | Q3 3 | 地域性への配慮、快適性の向上 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | 3.1 | Q3 3 | 地域性への配慮、快適性の向上 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 3.1 | Q3 3 | 地域性への配慮、快適性の向上 | 0
3.2 | 敷地内温熱環境の向上 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.5 | 0 |  | 3.2 | 敷地内温熱環境の向上 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.2 | Q3 3 | 敷地内温熱環境の向上 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 3.2 | Q3 3 | 敷地内温熱環境の向上 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 3.2 | Q3 3 | 敷地内温熱環境の向上 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 3.2 | Q3 3 | 敷地内温熱環境の向上 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | 3.2 | Q3 3 | 敷地内温熱環境の向上 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 3.2 | Q3 3 | 敷地内温熱環境の向上 | 0
0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | Q | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Q |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Q | [15 empty] | Q | [16 empty] | Q |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Q |  | 0
LR | 建築物の環境負荷低減性 |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 | LR 建築物の環境負荷低減性 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | LR |  | 建築物の環境負荷低減性 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LR |  | 建築物の環境負荷低減性 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LR |  | 建築物の環境負荷低減性 | [13 empty] | LR |  | 建築物の環境負荷低減性 | [14 empty] | LR |  | 建築物の環境負荷低減性 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LR |  | 建築物の環境負荷低減性 | 0
LR1 | エネルギー | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.4 | 0 | LR1 | エネルギー |  |  |  | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 小中高 | 病院 | ホテル | 集合住宅 | 病院o | ホテルo | 集合住宅o | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | LR1 | LR | エネルギー | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | LR1 | LR | エネルギー | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | LR1 | LR | エネルギー | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | LR1 | LR | エネルギー | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  |  | LR1 | LR | エネルギー | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | LR1 | LR | エネルギー | 0.55
1 | 建物外皮の熱負荷抑制 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.2 | 0 | 1 | 建物外皮の熱負荷抑制 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1 | LR1 | 建物外皮の熱負荷抑制 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 1 | LR1 | 建物外皮の熱負荷抑制 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 1 | LR1 | 建物外皮の熱負荷抑制 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 1 | LR1 | 建物外皮の熱負荷抑制 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 1 | LR1 | 建物外皮の熱負荷抑制 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 1 | LR1 | 建物外皮の熱負荷抑制 | 0.2 | bar: 事務所 to ホテル
2 | 自然エネルギー利用 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.1 | 0 | 2 | 自然エネルギー利用 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2 | LR1 | 自然エネルギー利用 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.125 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 2 | LR1 | 自然エネルギー利用 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.125 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 2 | LR1 | 自然エネルギー利用 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.125 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 2 | LR1 | 自然エネルギー利用 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.125 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  |  | 2 | LR1 | 自然エネルギー利用 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.125 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 2 | LR1 | 自然エネルギー利用 | 0.1
0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | LR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | LR | 実施・竣工 | [14 empty] | LR | 定量評価 | [14 empty] | LR | [16 empty] | LR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | LR |  | 0
0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | LR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | LR | 基本 | [14 empty] | LR | 定性評価 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | LR | [16 empty] | LR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | LR |  | 0
2.1 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.1 | LR1 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | LR1 2 | 自然エネルギーの直接利用 | [13 empty] | 2.1 | LR1 2 | 自然エネルギーの直接利用 | [13 empty] | 2.1 | LR1 2 | [15 empty] | 2.1 | LR1 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | LR1 2 |  | 0
2.2 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.2 | LR1 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | LR1 2 | 自然エネルギーの変換利用 | [13 empty] | 2.2 | LR1 2 | 自然エネルギーの変換利用 | [13 empty] | 2.2 | LR1 2 | [15 empty] | 2.2 | LR1 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | LR1 2 |  | 0
3 | 設備システムの高効率化 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.5 | 0 | 3 | 設備システムの高効率化 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3 | LR1 | 設備システムの高効率化 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.625 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 3 | LR1 | 設備システムの高効率化 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.625 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 3 | LR1 | 設備システムの高効率化 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.625 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 3 | LR1 | 設備システムの高効率化 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.625 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | 3 | LR1 | 設備システムの高効率化 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.625 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 3 | LR1 | 設備システムの高効率化 | 0.5 | bar: 事務所 to ホテル
3a.3b | 非住宅部分 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 1 | 0 |  |  | 集合住宅以外の評価(3a.3b) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3a.3b | LR1 3 | 非住宅部分 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 3a | LR1 3 | ERRによる評価 | [13 empty] | 3a | LR1 3 | 非住宅部分 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 3a.3b | LR1 3 | 非住宅部分 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [5 empty] | 3a.3b | LR1 3 | 非住宅部分 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 3a.3b | LR1 3 | 非住宅部分 | 1 | bar: 事務所 to ホテル
3b.c | 集合住宅の評価 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 |  |  | 集合住宅の評価(3c) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3b.c | LR1 3 | 集合住宅の評価 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3b | LR1 3 | ERR以外による評価 | [13 empty] | 3b | LR1 3 | 集合住宅の評価 | [9 empty] | 1 |  |  |  | 3b.c | LR1 3 | 集合住宅の評価 | [9 empty] | 1 |  |  |  |  | 3b.c | LR1 3 | 集合住宅の評価 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3b.c | LR1 3 | 集合住宅の評価 | 0 | bar: 事務所 to ホテル
3.1 | 空調設備 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  | 3.1 | 空調設備 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.1 | LR1 3b | 空調設備 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | LR1 3b | 空調設備 | [6 empty] | 0.65 | [6 empty] | 3.1 | LR1 3b | 空調設備 | [6 empty] | 0.65 | [6 empty] | 3.1 | LR1 3b | 空調設備 | [13 empty] | 127 | 3.1 | LR1 3b |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | LR1 3b |  | 0
3.2 | 換気設備 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  | 3.2 | 換気設備 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.2 | LR1 3b | 換気設備 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | LR1 3b | 換気設備 | [6 empty] | 0.1 | [6 empty] | 3.2 | LR1 3b | 換気設備 | [6 empty] | 0.1 | [6 empty] | 3.2 | LR1 3b | 換気設備 | [13 empty] | 128 | 3.2 | LR1 3b |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | LR1 3b |  | 0
3.3 | 照明設備 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  | 3.3 | 照明設備 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.3 | LR1 3b | 照明設備 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | LR1 3b | 照明設備 | [6 empty] | 0.2 | [6 empty] | 3.3 | LR1 3b | 照明設備 | [6 empty] | 0.2 | [6 empty] | 3.3 | LR1 3b | 照明設備 | [13 empty] | 129 | 3.3 | LR1 3b |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | LR1 3b |  | 0
3.4 | 給湯設備 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  | 3.4 | 給湯設備 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.4 | LR1 3b | 給湯設備 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | LR1 3b | 給湯設備 | [6 empty] | 0.05 | [6 empty] | 3.4 | LR1 3b | 給湯設備 | [6 empty] | 0.05 | [6 empty] | 3.4 | LR1 3b | 給湯設備 | [13 empty] | 130 | 3.4 | LR1 3b |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | LR1 3b |  | 0
3.5 | 昇降機設備 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  | 3.5 | 昇降機設備 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.5 | LR1 3b | 昇降機設備 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | LR1 3b | 昇降機設備 | [13 empty] | 3.5 | LR1 3b | 昇降機設備 | [13 empty] | 3.5 | LR1 3b | 昇降機設備 | [13 empty] | 131 | 3.5 | LR1 3b |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | LR1 3b |  | 0
0 | 0 |  |  | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  | 3.6 | エネルギー利用効率化設備 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | LR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | LR | [15 empty] | LR | [15 empty] | LR | [14 empty] | 132 |  | LR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | LR |  | 0
4 | 効率的運用 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.2 | 0 | 4 | 効率的運用 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 4 | LR1 | 効率的運用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 4 | LR1 | 効率的運用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 4 | LR1 | 効率的運用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 4 | LR1 | 効率的運用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 133 | 4 | LR1 | 効率的運用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 4 | LR1 | 効率的運用 | 0.2 | bar: 事務所 to ホテル
4.1 | 住宅以外の評価 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1 | 0 |  |  | 集合住宅以外の評価 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 4.1 | LR1 4 | 住宅以外の評価 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 4.1 | LR1 4 | 住宅以外の評価 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 4.1 | LR1 4 | 住宅以外の評価 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 4.1 | LR1 4 | 住宅以外の評価 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | 134 | 4.1 | LR1 4 | 住宅以外の評価 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 4.1 | LR1 4 | 住宅以外の評価 | 1 | bar: 事務所 to ホテル
4.1.1 | モニタリング | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.5 | 0 |  |  | 4.1 | モニタリング |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 4.1.1 | LR1 4.1 | モニタリング | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 4.1.1 | LR1 4.1 | モニタリング | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | 4.1.1 | LR1 4.1 | モニタリング | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | 4.1.1 | LR1 4.1 | モニタリング | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [5 empty] | 4.1.1 | LR1 4.1 | モニタリング | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 4.1.1 | LR1 4.1 | モニタリング | 0.5
4.1.2 | 運用管理体制 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.5 | 0 |  |  | 4.2 | 運用管理体制 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 4.1.2 | LR1 4.1 | 運用管理体制 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 4.1.2 | LR1 4.1 | 運用管理体制 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | 4.1.2 | LR1 4.1 | 運用管理体制 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | 4.1.2 | LR1 4.1 | 運用管理体制 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [5 empty] | 4.1.2 | LR1 4.1 | 運用管理体制 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 4.1.2 | LR1 4.1 | 運用管理体制 | 0.5
4.2 | 住宅の評価 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 |  |  | 集合住宅の評価 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 4.2 | LR1 4 | 住宅の評価 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4.2 | LR1 4 | 住宅の評価 | [9 empty] | 1 |  |  |  | 4.2 | LR1 4 | 住宅の評価 | [9 empty] | 1 |  |  |  | 4.2 | LR1 4 | 住宅の評価 | [9 empty] | 1 |  |  |  |  | 4.2 | LR1 4 | 住宅の評価 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4.2 | LR1 4 | 住宅の評価 | 0 | bar: 事務所 to ホテル
4.2.1 | モニタリング | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 4.1 | モニタリング |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 4.2.1 | LR1 4.2 | モニタリング | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 4.2.1 | LR1 4.2 | 住まい方の提示 | [9 empty] | 0.5 |  |  |  | 4.2.1 | LR1 4.2 | モニタリング | [9 empty] | 0.5 |  |  |  | 4.2.1 | LR1 4.2 | モニタリング | [9 empty] | 0.5 |  |  |  |  | 4.2.1 | LR1 4.2 | モニタリング | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 4.2.1 | LR1 4.2 | モニタリング | 0
4.2.2 | 運用管理体制 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 4.2 | 運用管理体制 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 4.2.2 | LR1 4.2 | 運用管理体制 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 4.2.2 | LR1 4.2 | エネルギーの管理と制御 | [9 empty] | 0.5 |  |  |  | 4.2.2 | LR1 4.2 | 運用管理体制 | [9 empty] | 0.5 |  |  |  | 4.2.2 | LR1 4.2 | 運用管理体制 | [9 empty] | 0.5 |  |  |  |  | 4.2.2 | LR1 4.2 | 運用管理体制 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 4.2.2 | LR1 4.2 | 運用管理体制 | 0
LR2 | 資源・マテリアル | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.3 | 0 | LR2 | 資源・マテリアル |  |  |  | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 小中高 | 病院 | ホテル | 集合住宅 | 病院o | ホテルo | 集合住宅o | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | LR2 | LR | 資源・マテリアル | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | LR2 | LR | 資源・マテリアル | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | LR2 | LR | 資源・マテリアル | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | LR2 | LR | 資源・マテリアル | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | LR2 | LR | 資源・マテリアル | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | LR2 | LR | 資源・マテリアル | 0.35
1 | 水資源保護 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.2 | 0 | 1 | 水資源保護 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1 | LR2 | 水資源保護 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 1 | LR2 | 水資源保護 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 1 | LR2 | 水資源保護 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 1 | LR2 | 水資源保護 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 1 | LR2 | 水資源保護 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 1 | LR2 | 水資源保護 | 0.3 | bar: 事務所 to ホテル
1.1 | 節水 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.4 | 0 |  | 1.1 | 節水 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.1 | LR2 1 | 節水 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 1.1 | LR2 1 | 節水 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | 1.1 | LR2 1 | 節水 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | 1.1 | LR2 1 | 節水 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  |  | 1.1 | LR2 1 | 節水 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 1.1 | LR2 1 | 節水 | 0.4
1.2 | 雨水利用・雑排水再利用 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.6 | 0 |  | 1.2 | 雨水利用・雑排水等の利用 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.2 | LR2 1 | 雨水利用・雑排水再利用 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0 | 0 | 1.2 | LR2 1 | 雨水利用・雑排水再利用 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  |  |  | 1.2 | LR2 1 | 雨水利用・雑排水再利用 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  |  |  | 1.2 | LR2 1 | 雨水利用・雑排水再利用 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  |  |  |  | 1.2 | LR2 1 | 雨水利用・雑排水再利用 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0 | 0 | 1.2 | LR2 1 | 雨水利用・雑排水再利用 | 0.6 | bar: 事務所 to ホテル
1.2.1 | 雨水利用システム導入の有無 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.7 | 0 |  |  | 1 | 雨水利用システム導入の有無 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.2.1 | LR2 1.2 | 雨水利用システム導入の有無 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 1.2.1 | LR2 1.2 | 雨水利用システム導入の有無 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 |  |  |  | 1.2.1 | LR2 1.2 | 雨水利用システム導入の有無 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 |  |  |  | 1.2.1 | LR2 1.2 | 雨水利用システム導入の有無 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 |  |  |  |  | 1.2.1 | LR2 1.2 | 雨水利用システム導入の有無 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 1.2.1 | LR2 1.2 | 雨水利用システム導入の有無 | 0.7
1.2.2 | 雑排水等再利用システム導入の有無 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.3 | 0 |  |  | 2 | 雑排水等利用システム導入の有無 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1.2.2 | LR2 1.2 | 雑排水等再利用システム導入の有無 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 1.2.2 | LR2 1.2 | 雑排水等再利用システム導入の有無 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 1.2.2 | LR2 1.2 | 雑排水等再利用システム導入の有無 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 1.2.2 | LR2 1.2 | 雑排水等再利用システム導入の有無 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | 1.2.2 | LR2 1.2 | 雑排水等再利用システム導入の有無 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 1.2.2 | LR2 1.2 | 雑排水等再利用システム導入の有無 | 0.3
2 | 非再生性資源の使用量削減 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.6 | 0 | 2 | 非再生性資源の使用量削減 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2 | LR2 | 非再生性資源の使用量削減 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0 | 0 | 2 | LR2 | 非再生性資源の使用量削減 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  |  |  | 2 | LR2 | 非再生性資源の使用量削減 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  |  |  | 2 | LR2 | 非再生性資源の使用量削減 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  |  |  |  | 2 | LR2 | 非再生性資源の使用量削減 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 2 | LR2 | 非再生性資源の使用量削減 | 0.5 | bar: 事務所 to ホテル
2.1 | 材料使用量の削減 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.1 | 0 |  | 2.1 | 材料使用量の削減 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.1 | LR2 2 | 材料使用量の削減 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 2.1 | LR2 2 | 材料使用量の削減 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 2.1 | LR2 2 | 材料使用量の削減 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 2.1 | LR2 2 | 材料使用量の削減 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  |  | 2.1 | LR2 2 | 材料使用量の削減 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | LR2 2 | 材料使用量の削減 | 0
2.2 | 既存建築躯体等の継続使用 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.2 | 0 |  | 2.2 | 既存建築躯体等の継続使用 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.2 | LR2 2 | 既存建築躯体等の継続使用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.2 | LR2 2 | 既存建築躯体等の継続使用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.2 | LR2 2 | 既存建築躯体等の継続使用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.2 | LR2 2 | 既存建築躯体等の継続使用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.2 | LR2 2 | 既存建築躯体等の継続使用 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | LR2 2 | 既存建築躯体等の継続使用 | 0
2.3 | 躯体材料におけるリサイクル材の使用 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.2 | 0 |  | 2.3 | 躯体材料におけるリサイクル材の使用 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.3 | LR2 2 | 躯体材料におけるリサイクル材の使用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.3 | LR2 2 | 躯体材料におけるリサイクル材の使用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.3 | LR2 2 | 躯体材料におけるリサイクル材の使用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.3 | LR2 2 | 躯体材料におけるリサイクル材の使用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.3 | LR2 2 | 躯体材料におけるリサイクル材の使用 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0 | 0 | 2.3 | LR2 2 | 躯体材料におけるリサイクル材の使用 | 0
2.4 | 躯体材料以外におけるリサイクル材の使用 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.2 | 0 |  | 2.4 | 躯体材料以外におけるリサイクル材の使用 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.4 | LR2 2 | 躯体材料以外におけるリサイクル材の使用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4 | LR2 2 | 躯体材料以外におけるリサイクル材の使用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.4 | LR2 2 | 躯体材料以外におけるリサイクル材の使用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.4 | LR2 2 | 躯体材料以外におけるリサイクル材の使用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.4 | LR2 2 | 躯体材料以外におけるリサイクル材の使用 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0 | 2.4 | LR2 2 | 躯体材料以外におけるリサイクル材の使用 | 0.2
2.5 | 持続可能な森林から産出された木材 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.1 | 0 |  | 2.5 | 持続可能な森林から産出された木材 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.5 | LR2 2 | 持続可能な森林から産出された木材 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 2.5 | LR2 2 | 持続可能な森林から産出された木材 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 2.5 | LR2 2 | 持続可能な森林から産出された木材 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 2.5 | LR2 2 | 持続可能な森林から産出された木材 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  |  | 2.5 | LR2 2 | 持続可能な森林から産出された木材 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0 | 2.5 | LR2 2 | 持続可能な森林から産出された木材 | 0.4
2.6 | 部材の再利用可能性向上への取組み | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.2 | 0 |  | 2.6 | 部材の再利用可能性向上への取組み |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.6 | LR2 2 | 部材の再利用可能性向上への取組み | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.6 | LR2 2 | 部材の再利用可能性向上への取組み | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.6 | LR2 2 | 部材の再利用可能性向上への取組み | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.6 | LR2 2 | 部材の再利用可能性向上への取組み | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.6 | LR2 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | LR2 2 | 部材の再利用可能性向上への取組み | 0.4
2.6 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 |  | 2.6 | 部材の再利用可能性向上への取組み |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.6 | LR2 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 2.6 | LR2 2 | [15 empty] | 2.6 | LR2 2 | 部材の再利用可能性向上への取組み（TC) | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0 | 0 | 0 | 2.6 | LR2 2 |  | 0
2.6.1 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 1 | 躯体のリサイクル・リユース |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.6.1 | LR2 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 2.6.1 | LR2 2.2 | [15 empty] | 2.6.1 | LR2 2.2 | 躯体のリサイクル・リユース | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.6.1 | LR2 2.2 |  | 0
2.6.2 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 2 | 屋根材のリサイクル・リユース |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.6.2 | LR2 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 2.6.2 | LR2 2.2 | [15 empty] | 2.6.2 | LR2 2.2 | 屋根材のリサイクル・リユース | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 2.6.2 | LR2 2.2 |  | 0
2.6.3 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 3 | 外壁材のリサイクル・リユース |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.6.3 | LR2 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 2.6.3 | LR2 2.2 | [15 empty] | 2.6.3 | LR2 2.2 | 外壁材のリサイクル・リユース | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 2.6.3 | LR2 2.2 |  | 0
2.6.4 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 4 | 内装材のリサイクル・リユース |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.6.4 | LR2 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 2.6.4 | LR2 2.2 | [15 empty] | 2.6.4 | LR2 2.2 | 内装材のリサイクル・リユース | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 2.6.4 | LR2 2.2 |  | 0
2.6.5 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 5 | 設備機器のリサイクル・リユース |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.6.5 | LR2 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 2.6.5 | LR2 2.2 | [15 empty] | 2.6.5 | LR2 2.2 | 設備機器のリサイクル・リユース | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 2.6.5 | LR2 2.2 |  | 0
2.6.6 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 6 | 外構資材のリユース |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.6.6 | LR2 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 2.6.6 | LR2 2.2 | [15 empty] | 2.6.6 | LR2 2.2 | 外構資材のリユース | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 2.6.6 | LR2 2.2 |  | 0
2.7 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  | 2.7 | 廃棄物発生量の最小化 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.7 | LR2 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 2.7 | LR2 2 | [15 empty] | 2.7 | LR2 2 | 廃棄物発生量の最小化 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.7 | LR2 2 |  | 0
3 | 汚染物質含有材料の使用回避 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.2 | 0 | 3 | 汚染物質含有材料の使用回避 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3 | LR2 | 汚染物質含有材料の使用回避 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 3 | LR2 | 汚染物質含有材料の使用回避 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 3 | LR2 | 汚染物質含有材料の使用回避 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3 | LR2 | 汚染物質含有材料の使用回避 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 3 | LR2 | 汚染物質含有材料の使用回避 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 3 | LR2 | 汚染物質含有材料の使用回避 | 0.2 | bar: 事務所 to ホテル
3.1 | 有害物質を含まない材料の使用 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.3 | 0 |  | 3.1 | 有害物質を含まない材料の使用 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.1 | LR2 3 | 有害物質を含まない材料の使用 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 3.1 | LR2 3 | 有害物質を含まない材料の使用 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 3.1 | LR2 3 | 有害物質を含まない材料の使用 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 3.1 | LR2 3 | 有害物質を含まない材料の使用 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | 3.1 | LR2 3 | 有害物質を含まない材料の使用 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 3.1 | LR2 3 | 有害物質を含まない材料の使用 | 0.6
3.2 | フロン・ハロンの回避 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.7 | 0 |  | 3.2 | フロン・ハロンの回避 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.2 | LR2 3 | フロン・ハロンの回避 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 3.2 | LR2 3 | フロン・ハロンの回避 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 3.2 | LR2 3 | フロン・ハロンの回避 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 |  |  |  | 3.2 | LR2 3 | フロン・ハロンの回避 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 |  |  |  |  | 3.2 | LR2 3 | フロン・ハロンの回避 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 3.2 | LR2 3 | フロン・ハロンの回避 | 0.4 | bar: 事務所 to ホテル
3.2.1 | 消火剤 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.33333 | 0 |  |  | 1 | 消火剤 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.2.1 | LR2 3.2 | 消火剤 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.2.1 | LR2 3.2 | 消火剤 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.2.1 | LR2 3.2 | 消火剤 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3.2.1 | LR2 3.2 | 消火剤 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  |  | 3.2.1 | LR2 3.2 | 消火剤 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.2.1 | LR2 3.2 | 消火剤 | 0
3.2.2 | 発泡剤（断熱材等） | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.33333 | 0 |  |  | 2 | 発泡剤（断熱材等） |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.2.2 | LR2 3.2 | 発泡剤（断熱材等） | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.2.2 | LR2 3.2 | 発泡剤（断熱材等） | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.2.2 | LR2 3.2 | 発泡剤（断熱材等） | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3.2.2 | LR2 3.2 | 発泡剤（断熱材等） | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  |  | 3.2.2 | LR2 3.2 | 発泡剤（断熱材等） | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.2.2 | LR2 3.2 | 発泡剤（断熱材等） | 0
3.2.3 | 冷媒 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.33333 | 0 |  |  | 3 | 冷媒 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.2.3 | LR2 3.2 | 冷媒 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.2.3 | LR2 3.2 | 冷媒 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.2.3 | LR2 3.2 | 冷媒 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3.2.3 | LR2 3.2 | 冷媒 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  |  | 3.2.3 | LR2 3.2 | 冷媒 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.2.3 | LR2 3.2 | 冷媒 | 1
LR3 | 敷地外環境 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.3 | 0 | LR3 | 敷地外環境 |  |  |  | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 小中高 | 病院 | ホテル | 集合住宅 | 病院o | ホテルo | 集合住宅o | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | LR3 | LR | 敷地外環境 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | LR3 | LR | 敷地外環境 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | LR3 | LR | 敷地外環境 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | LR3 | LR | 敷地外環境 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | LR3 | LR | 敷地外環境 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | LR3 | LR | 敷地外環境 | 0.1
1 | 地球温暖化への配慮 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.33333 | 0 | 1 | 地球温暖化への配慮 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1 | LR3 | 地球温暖化への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 1 | LR3 | 地球温暖化への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 1 | LR3 | 地球温暖化への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 1 | LR3 | 地球温暖化への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  |  | 1 | LR3 | 地球温暖化への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 1 | LR3 | 地球温暖化への配慮 | 0 | bar: 事務所 to ホテル
2 | 地域環境への配慮 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.33333 | 0 | 2 | 地域環境への配慮 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2 | LR3 | 地域環境への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 2 | LR3 | 地域環境への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 2 | LR3 | 地域環境への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 2 | LR3 | 地域環境への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  |  | 2 | LR3 | 地域環境への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 2 | LR3 | 地域環境への配慮 | 1 | bar: 事務所 to ホテル
2.1 | 大気汚染防止 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.25 | 0 |  | 2.1 | 大気汚染防止 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.1 | LR3 2 | 大気汚染防止 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.1 | LR3 2 | 大気汚染防止 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.1 | LR3 2 | 大気汚染防止 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.1 | LR3 2 | 大気汚染防止 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  |  | 2.1 | LR3 2 | 大気汚染防止 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.1 | LR3 2 |  | 0
2.2 | 温熱環境悪化の改善 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.5 | 0 |  | 2.2 | 温熱環境悪化の改善 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.2 | LR3 2 | 温熱環境悪化の改善 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 2.2 | LR3 2 | 温熱環境悪化の改善 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 2.2 | LR3 2 | 温熱環境悪化の改善 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 2.2 | LR3 2 | 温熱環境悪化の改善 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | 2.2 | LR3 2 | 温熱環境悪化の改善 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 2.2 | LR3 2 |  | 0
2.3 | 地域インフラへの負荷抑制 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.25 | 0 |  | 2.3 | 地域インフラへの負荷抑制 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.3 | LR3 2 | 地域インフラへの負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.3 | LR3 2 | 地域インフラへの負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3 | LR3 2 | 地域インフラへの負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3 | LR3 2 | 地域インフラへの負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  |  | 2.3 | LR3 2 | 地域インフラへの負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.3 | LR3 2 |  | 0 | bar: 事務所 to ホテル
2.3.1 | 雨水排水負荷低減 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.25 | 0 |  |  | 1 | 雨水排水負荷低減 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.3.1 | LR3 2.3 | 雨水排水負荷低減 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.3.1 | LR3 2.3 | 雨水排水負荷低減 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3.1 | LR3 2.3 | 雨水排水負荷低減 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3.1 | LR3 2.3 | 雨水排水負荷低減 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  |  | 2.3.1 | LR3 2.3 | 雨水排水負荷低減 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.3.1 | LR3 2.3 |  | 0
2.3.2 | 汚水処理負荷抑制 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.25 | 0 |  |  | 2 | 汚水処理負荷抑制 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.3.2 | LR3 2.3 | 汚水処理負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.3.2 | LR3 2.3 | 汚水処理負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3.2 | LR3 2.3 | 汚水処理負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3.2 | LR3 2.3 | 汚水処理負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  |  | 2.3.2 | LR3 2.3 | 汚水処理負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.3.2 | LR3 2.3 |  | 0
2.3.3 | 交通負荷抑制 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.25 | 0 |  |  | 3 | 交通負荷抑制 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.3.3 | LR3 2.3 | 交通負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.3.3 | LR3 2.3 | 交通負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3.3 | LR3 2.3 | 交通負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3.3 | LR3 2.3 | 交通負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  |  | 2.3.3 | LR3 2.3 | 交通負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.3.3 | LR3 2.3 |  | 0
2.3.4 | 廃棄物処理負荷抑制 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.25 | 0 |  |  | 4 | 廃棄物処理負荷抑制 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2.3.4 | LR3 2.3 | 廃棄物処理負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.3.4 | LR3 2.3 | 廃棄物処理負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3.4 | LR3 2.3 | 廃棄物処理負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3.4 | LR3 2.3 | 廃棄物処理負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  |  | 2.3.4 | LR3 2.3 | 廃棄物処理負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.3.4 | LR3 2.3 |  | 0
0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  | 2.1 | 廃棄物処理負荷抑制 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [65 empty] | 2.3.4 | LR3 2.3 | 廃棄物処理負荷抑制 | 1
3 | 周辺環境への配慮 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.33333 | 0 | 3 | 周辺環境への配慮 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - | #REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3 | LR3 | 周辺環境への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3 | LR3 | 周辺環境への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3 | LR3 | 周辺環境への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3 | LR3 | 周辺環境への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  |  | 3 | LR3 | 周辺環境への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3 | LR3 | 周辺環境への配慮 | 0 | bar: 事務所 to ホテル
3.1 | 騒音・振動・悪臭の防止 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.4 | 0 |  | 3.1 | 騒音・振動・悪臭の防止 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.1 | LR3 3 | 騒音・振動・悪臭の防止 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 3.1 | LR3 3 | 騒音・振動・悪臭の防止 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | 3.1 | LR3 3 | 騒音・振動・悪臭の防止 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | 3.1 | LR3 3 | 騒音・振動・悪臭の防止 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  |  | 3.1 | LR3 3 | 騒音・振動・悪臭の防止 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 3.1 | LR3 3 |  | 0 | bar: 事務所 to ホテル
3.1.1 | 騒音 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.33333 | 0 |  |  | 1 | 騒音 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.1.1 | LR3 3.1 | 騒音 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.1.1 | LR3 3.1 | 騒音 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3.1.1 | LR3 3.1 | 騒音 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3.1.1 | LR3 3.1 | 騒音 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  |  | 3.1.1 | LR3 3.1 | 騒音 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.1.1 | LR3 3.1 |  | 0
3.1.2 | 振動 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.33333 | 0 |  |  | 2 | 振動 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.1.2 | LR3 3.1 | 振動 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.1.2 | LR3 3.1 | 振動 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3.1.2 | LR3 3.1 | 振動 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3.1.2 | LR3 3.1 | 振動 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  |  | 3.1.2 | LR3 3.1 | 振動 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.1.2 | LR3 3.1 |  | 0
3.1.3 | 悪臭 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.33333 | 0 |  |  | 3 | 悪臭 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.1.3 | LR3 3.1 | 悪臭 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.1.3 | LR3 3.1 | 悪臭 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3.1.3 | LR3 3.1 | 悪臭 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3.1.3 | LR3 3.1 | 悪臭 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  |  | 3.1.3 | LR3 3.1 | 悪臭 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.1.3 | LR3 3.1 |  | 0
3.2 | 風害・砂塵、日照阻害の抑制 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.4 | 0 |  | 3.2 | 風害、砂塵、日照阻害の抑制 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.2 | LR3 3 | 風害・砂塵、日照阻害の抑制 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 3.2 | LR3 3 | 風害、日照阻害の抑制 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | 3.2 | LR3 3 | 風害・砂塵、日照阻害の抑制 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | 3.2 | LR3 3 | 風害・砂塵、日照阻害の抑制 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  |  | 3.2 | LR3 3 | 風害・砂塵、日照阻害の抑制 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 3.2 | LR3 3 |  | 0 | bar: 事務所 to ホテル
3.2.1 | 風害の抑制 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.7 | 0 |  |  | 1 | 風害の抑制 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.2.1 | LR3 3.2 | 風害の抑制 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 3.2.1 | LR3 3.2 | 風害の抑制 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.7 | 0.7 | 0.7 |  |  |  | 3.2.1 | LR3 3.2 | 風害の抑制 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.7 | 0.7 | 0.7 |  |  |  | 3.2.1 | LR3 3.2 | 風害の抑制 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.7 | 0.7 | 0.7 |  |  |  |  | 3.2.1 | LR3 3.2 | 風害の抑制 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 3.2.1 | LR3 3.2 |  | 0
3.2.2 | 砂塵の抑制 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0 | 0 |  |  | 2 | 砂塵の抑制 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.2.2 | LR3 3.2 | 砂塵の抑制 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2.3 | LR3 3.3 | 砂塵の抑制 | [6 empty] | 0.2 | [6 empty] | 3.2.2 | LR3 3.2 | 砂塵の抑制 | [6 empty] | 0.2 | [6 empty] | 3.2.2 | LR3 3.2 | 砂塵の抑制 | [6 empty] | 0.2 | [7 empty] | 3.2.2 | LR3 3.2 | 砂塵の抑制 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2.2 | LR3 3.2 |  | 0
3.2.3 | 日照阻害の抑制 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.3 | 0 |  |  | 3 | 日照阻害の抑制 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.2.3 | LR3 3.2 | 日照阻害の抑制 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 3.2.2 | LR3 3.2 | 日照阻害の抑制 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.3 | 0.3 | 0.3 |  |  |  | 3.2.3 | LR3 3.2 | 日照阻害の抑制 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.3 | 0.3 | 0.3 |  |  |  | 3.2.3 | LR3 3.2 | 日照阻害の抑制 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.3 | 0.3 | 0.3 |  |  |  |  | 3.2.3 | LR3 3.2 | 日照阻害の抑制 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 3.2.3 | LR3 3.2 |  | 0
3.3 | 光害の抑制 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0.2 | 0 |  | 3.3 | 光害の抑制 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | - | - | - | - |  | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.3 | LR3 3 | 光害の抑制 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 3.3 | LR3 3 | 光害の抑制 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3 | LR3 3 | 光害の抑制 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3 | LR3 3 | 光害の抑制 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 3.3 | LR3 3 | 光害の抑制 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 3.3 | LR3 3 |  | 0 | bar: 事務所 to ホテル
3.3.1 | 屋外照明及び屋内照明のうち外に漏れる光への対策 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.7 | 0 |  |  | 1 | 屋外照明及び屋内照明のうち外に漏れる光への対策 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.3.1 | LR3 3.3 | 屋外照明及び屋内照明のうち外に漏れる光への対策 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 3.3.1 | LR3 3.3 | 屋外照明及び屋内照明のうち外に漏れる光への対策 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 |  |  |  | 3.3.1 | LR3 3.3 | 屋外照明及び屋内照明のうち外に漏れる光への対策 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 |  |  |  | 3.3.1 | LR3 3.3 | 屋外照明及び屋内照明のうち外に漏れる光への対策 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 |  |  |  |  | 3.3.1 | LR3 3.3 | 屋外照明及び屋内照明のうち外に漏れる光への対策 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 3.3.1 | LR3 3.3 |  | 0
3.3.2 | 昼光の建物外壁による反射光（グレア）への対策 | #REF! | #REF! | #REF! | #REF! |  |  | #REF! | #REF! | 0.3 | 0 |  |  | 2 | 昼光の建物外壁による反射光（グレア）への対策 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3.3.2 | LR3 3.3 | 昼光の建物外壁による反射光（グレア）への対策 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 3.3.2 | LR3 3.3 | 昼光の建物外壁による反射光（グレア）への対策 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 3.3.2 | LR3 3.3 | 昼光の建物外壁による反射光（グレア）への対策 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 3.3.2 | LR3 3.3 | 昼光の建物外壁による反射光（グレア）への対策 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | 3.3.2 | LR3 3.3 | 昼光の建物外壁による反射光（グレア）への対策 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 3.3.2 | LR3 3.3 |  | 0
LR1「１．建物外皮の熱負荷抑制」「３．設備システムの高効率化」は、CASBEE-建築（新築）評価ソフト「計画書シート」で評価します。

## Score
| CASBEE for Building Design (New Construction) 2024 Edition | [11 empty] | n Manual: | [5 empty] | CASBEE for Building Design (New Construction) 2024 Edition
| XXX Building | [11 empty] | n Software: |  |  | CASBEE-BD_NCe_2024_v1.21 | [5 empty] | 2 | NC
| Score Sheet |  |  | Execution design stage | [15 empty] | 採点シートの 採点結果 | [6 empty] | 建物全体・共用部分 | 住居・宿泊部分
[7 empty] | Summary of environmentally conscious efforts in design | [7 empty] | Entire Building & Common areas |  | Dwelling & Accommodation |  |  |  |  | 建物全体 |  | 住居宿泊 |  |  | 1 | 0
| Assessment Categories | [13 empty] | Score | weight | Score | weight | Total | 建物全体 | 住居宿泊 | 採点シートの 採点結果 | 重み 係数 | 採点シートの 採点結果 | 重み 係数 | 全体 | weight(set) | weight(set)
| Q: Environmental Quality of Building | [17 empty] | 3 | [6 empty] | 3 | 0 | 0 |  |  | Environmental Quality of Building
| Q1 Indoor Environment | [14 empty] | 0.4 |  | 0 | 3 |  |  |  | 0.4 |  |  | 3 | 0.4 | 0 | No.14 | No.15 | Indoor Environment
| 1 | Sound Environment | [12 empty] | 3 | 0.15 | 0 | 0 | 3 |  |  | 3 | 0.15 | 0 | 0 | 3 | 0.15 | 0 |  |  | Sound Environment
|  | 1.1 | Indoor Noise Level |  |  |  | 0 | [7 empty] | 3 | 0.4 | 0 | 0 |  | 3 | 3 | 3 | 0.4 | 0 | 0 |  | 0.4 | 0 |  |  | Indoor Noise Level
・LR2/3.2.3 発泡材 |  |  | 1 | Background noise level | [10 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | 0 |  |  | Background noise level
|  |  | 2 | Equipment noise | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  |  | Equipment noise
|  | 1.2 | Sound Insulation | [11 empty] | 3 | 0.4 | 0 | 0 |  |  |  | 3 | 0.4 | 0 | 0 |  | 0.4 | 0 |  |  | Sound Insulation
|  |  | 1 | Sound Insulation of Openings |  |  | 0 | [7 empty] | 3 | 0.6 | 0 | 0 |  | 3 | 0 | 3 | 0.6 | 0 | 0 |  | 0.6 | 0 |  |  | Sound Insulation of Openings
|  |  | 2 | Sound Insulation of Partition Walls |  |  | 0 | [7 empty] | 3 | 0.4 | 0 | 0 |  | 3 | 3 | 3 | 0.4 | 0 | 0 |  | 0.4 | 0 |  |  | Sound Insulation of Partition Walls
|  |  | 3 | Sound Insulation Performance of Floor Slabs (light-weight impact source) |  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 |  | 3 | 3 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | Sound Insulation Performance of Floor Slabs (light-weight impact source)
|  |  | 4 | Sound Insulation Performance of Floor Slabs (heavy-weight impact source) |  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 |  | 3 | 3 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | Sound Insulation Performance of Floor Slabs (heavy-weight impact source)
|  | 1.3 | Sound Absorption |  |  |  | 0 | [7 empty] | 3 | 0.2 | 0 | 0 |  | 3 | 3 | 3 | 0.2 | 0 | 0 |  | 0.2 | 0 |  |  | Sound Absorption
| 2 | Thermal Comfort | [12 empty] | 3 | 0.35 | 0 | 0 | 3 |  |  | 3 | 0.35 | 0 | 0 | 3 | 0.35 | 0 |  |  | Thermal Comfort
|  | 2.1 | Room Temperature Control | [11 empty] | 3 | 0.625 | 0 | 0 |  |  |  | 3 | 0.625 | 0 | 0 |  | 0.5 | 0 |  |  | Room Temperature Control
|  |  | 1 | Room Temperature |  |  | 0 | [7 empty] | 3 | 0.375 | 0 | 0 |  | 3 | 3 | 3 | 0.375 | 0 | 0 |  | 0.375 | 0 |  |  | Room Temperature
|  |  | 2 | Variable Loads and Following-up Control | [10 empty] | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | Variable Loads and Following-up Control
|  |  | 2 | Perimeter Performance |  |  | sample input; Introduction of airflow windows | [7 empty] | 3 | 0.25 | 0 | 0 |  | 3 | 3 | 3 | 0.25 | 0 | 0 |  | 0.25 | 0 |  |  | Perimeter Performance
|  |  | 3 | Zoned Control |  |  | 0 | [7 empty] | 3 | 0.375 | 0 | 0 |  | 3 |  | 3 | 0.375 | 0 | 0 |  | 0.375 | 0 |  |  | Zoned Control
|  |  | 5 | Temperature and Humidity Control | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | Temperature and Humidity Control
|  |  | 6 | Individual Control | [10 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | Individual Control
|  |  | 7 | Allowance for After-hours Air Conditioning | [10 empty] | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | Allowance for After-hours Air Conditioning
|  |  | 8 | Monitoring Systems | [10 empty] | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | Monitoring Systems
|  | 2.2 | Humidity Control |  |  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 |  | 0 | 3 | 0 | 0 | 0 | 0 |  | 0.2 | 0 |  |  | Humidity Control
|  | 2.3 | Type of Air Conditioning System |  |  |  | 0 | [7 empty] | 3 | 0.375 | 0 | 0 |  | 3 | 3 | 3 | 0.375 | 0 | 0 |  | 0.3 | 0 |  |  | Type of Air Conditioning System
|  | 2.3 | 空調方式 | [11 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0
|  |  | 1 | 上下温度差 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0
|  |  | 2 | 平均気流速度 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0
| 3 | Lighting & Illumination | [12 empty] | 3 | 0.25 | 0 | 0 | 3 |  |  | 3 | 0.25 | 0 | 0 | 3 | 0.25 | 0 |  |  | Lighting & Illumination
|  | 3.1 | Daylighting | [11 empty] | 3 | 0.3 | 0 | 0 |  |  |  | 3 | 0.3 | 0 | 0 |  | 0.3 | 0 |  |  | Daylighting
|  |  | 1 | Daylight Factor |  |  | 0 | [7 empty] | 3 | 0.6 | 0 | 0 |  | 3 | 3 | 3 | 0.6 | 0 | 0 |  | 0.6 | 0 |  |  | Daylight Factor
|  |  | 2 | Openings by Orientation |  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 |  |  | 3 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | Openings by Orientation
|  |  | 3 | Daylight Devices |  |  | 0 | [7 empty] | 3 | 0.4 | 0 | 0 |  | 3 | 3 | 3 | 0.4 | 0 | 0 |  | 0.4 | 0 |  |  | Daylight Devices
|  | 3.2 | Anti-glare Measures | [11 empty] | 3 | 0.3 | 0 | 0 |  |  |  | 3 | 0.3 | 0 | 0 |  | 0.3 | 0 |  |  | Anti-glare Measures
|  |  | 1 | Glare from Light Fixtures | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  |  | Glare from Light Fixtures
|  |  | 1 | Daylight Control |  |  | 0 | [7 empty] | 3 | 1 | 0 | 0 |  | 3 | 3 | 3 | 1 | 0 | 0 |  | 1 | 0 |  |  | Daylight Control
|  |  | 2 | 映り込み対策 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | Reflection Control
|  | 3.3 | Illuminance Level |  |  |  | 0 | [7 empty] | 3 | 0.15 | 0 | 0 |  | 3 | 3 | 3 | 0.15 | 0 | 0 |  | 0.15 | 0 |  |  | Illuminance Level
|  |  | 1 | 照度 | [10 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | 照度
|  |  | 2 | 照度均斉度 | [10 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | 照度均斉度
|  | 3.4 | Lighting Controllability |  |  |  | 0 | [7 empty] | 3 | 0.25 | 0 | 0 |  | 3 | 3 | 3 | 0.25 | 0 | 0 |  | 0.25 | 0 |  |  | Lighting Controllability
| 4 | Air Quality | [12 empty] | 3 | 0.25 | 0 | 0 | 3 |  |  | 3 | 0.25 | 0 | 0 | 3 | 0.25 | 0 |  |  | Air Quality
|  | 4.1 | Source Control | [11 empty] | 3 | 0.5 | 0 | 0 |  |  |  | 3 | 0.5 | 0 | 0 |  | 0.5 | 0 |  |  | Source Control
|  |  | 1 | Chemical Pollutants |  |  | 0 | [7 empty] | 3 | 1 | 0 | 0 |  | 3 | 3 | 3 | 1 | 0 | 0 |  | 1 | 0 |  |  | Chemical Pollutants
|  |  | 2 | Asbestos | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | Asbestos
|  |  | 3 | Mites, Mold etc. | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  |  | Mites, Mold etc.
|  |  | 4 | Legionella | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  |  | Legionella
|  | 4.2 | Ventilation | [11 empty] | 3 | 0.3 | 0 | 0 |  |  |  | 3 | 0.3 | 0 | 0 |  | 0.3 | 0 |  |  | Ventilation
|  |  | 1 | Ventilation Rate |  |  | 0 | [7 empty] | 3 | 0.33333 | 0 | 0 |  | 3 | 3 | 3 | 0.33333 | 0 | 0 |  | 0.33333 | 0 |  |  | Ventilation Rate
|  |  | 2 | Natural Ventilation Performance |  |  | 0 | [7 empty] | 3 | 0.33333 | 0 | 0 |  | 3 | 3 | 3 | 0.33333 | 0 | 0 |  | 0.33333 | 0 |  |  | Natural Ventilation Performance
|  |  | 3 | Consideration for Outside Air Intake |  |  | 0 | [7 empty] | 3 | 0.33333 | 0 | 0 |  | 3 | 3 | 3 | 0.33333 | 0 | 0 |  | 0.33333 | 0 |  |  | Consideration for Outside Air Intake
|  |  | 4 | Air Supply Planning | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 |  |  | Air Supply Planning
|  | 4.3 | Operation Plan | [11 empty] | 3 | 0.2 | 0 | 0 |  |  |  | 3 | 0.2 | 0 | 0 |  | 0.2 | 0 |  |  | Operation Plan
|  |  | 1 | CO2 Monitoring |  |  | 0 | [7 empty] | 3 | 0.5 | 0 | 0 |  | 3 |  | 3 | 0.5 | 0 | 0 |  | 0.5 | 0 |  |  | CO2 Monitoring
|  |  | 2 | Control of Smoking |  |  | 0 | [7 empty] | 3 | 0.5 | 0 | 0 |  | 3 |  | 3 | 0.5 | 0 | 0 |  | 0.5 | 0 |  |  | Control of Smoking
| Q2 Quality of Service | [13 empty] | 0 | 0.3 | 0 | 0 | 3 |  |  |  | 0.3 |  |  | 3 | 0.3 | 0 | No.14 | No.15 | Quality of Service
| 1 | Service Ability | [12 empty] | 3 | 0.4 | 0 | 0 | 3 |  |  | 3 | 0.4 | 0 | 0 | 3 | 0.4 | 0 |  |  | Service Ability
|  | 1.1 | Functionality & Usability | [11 empty] | 3 | 0.4 | 0 | 0 |  |  |  | 3 | 0.4 | 0 | 0 |  | 0.4 | 0 |  |  | Functionality & Usability
|  |  | 1 | Provision of Space & Storage |  |  | 0 | [7 empty] | 3 | 0.33333 | 0 | 0 |  | 3 | 3 | 3 | 0.33333 | 0 | 0 |  | 0.33333 | 0 |  |  | Provision of Space & Storage
|  |  | 2 | Use of Advanced Information System |  |  | 0 | [7 empty] | 3 | 0.33333 | 0 | 0 |  | 3 | 3 | 3 | 0.33333 | 0 | 0 |  | 0.33333 | 0 |  |  | Use of Advanced Information System
|  |  | 3 | Barrier-free Planning |  |  | 0 | [7 empty] | 3 | 0.33333 | 0 | 0 |  | 3 |  | 3 | 0.33333 | 0 | 0 |  | 0.33333 | 0 |  |  | Barrier-free Planning
|  | 1.2 | Amenity | [11 empty] | 3 | 0.3 | 0 | 0 |  |  |  | 3 | 0.3 | 0 | 0 |  | 0.3 | 0 |  |  | Amenity
|  |  | 1 | Perceived Spaciousness & Access to View |  |  | 0 | [7 empty] | 3 | 0.33333 | 0 | 0 |  | 3 | 3 | 3 | 0.33333 | 0 | 0 |  | 0.33333 | 0 |  |  | Perceived Spaciousness & Access to View
[6 empty] | （窓の配置） | [8 empty] | 0 | 0 | 0 |  |  | 100 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0
|  |  | 2 | Space for Refreshment |  |  | 0 | [7 empty] | 3 | 0.33333 | 0 | 0 |  | 3 |  | 3 | 0.33333 | 0 | 0 |  | 0.33333 | 0 |  |  | Space for Refreshment
|  |  | 3 | Décor Planning |  |  | 0 | [7 empty] | 3 | 0.33333 | 0 | 0 |  | 3 | 1 | 3 | 0.33333 | 0 | 0 |  | 0.33333 | 0 |  |  | Décor Planning
[15 empty] | 100 | 0 | 0 |  |  | 100 |  | 100 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0
|  | 1.3 | Maintenance Management | [11 empty] | 3 | 0.3 | 0 | 0 |  |  |  | 3 | 0.3 | 0 | 0 |  | 0.3 | 0 |  |  | Maintenance Management
|  |  | 1 | Design that Considers Maintenance Management |  |  | 0 | [7 empty] | 3 | 0.5 | 0 | 0 |  | 3 |  | 3 | 0.5 | 0 | 0 |  | 0.5 | 0 |  |  | Design that Considers Maintenance Management
|  |  | 2 | Securing Maintenance Management Functions |  |  | 0 | [7 empty] | 3 | 0.5 | 0 | 0 |  | 3 |  | 3 | 0.5 | 0 | 0 |  | 0.5 | 0 |  |  | Securing Maintenance Management Functions
|  |  | 3 |  |  |  | 0 | [7 empty] | 3 | 0 | 0 | 0 |  | 3 |  | 3 | 0 | 0 | 0 |  | 0 | 0 |  |  | Sanitation management operations
| 2 | Durability & Reliability | [12 empty] | 3 | 0.3 | 0 | 0 | 3 |  |  | 3 | 0.3 | 0 | 0 | 3 | 0.3 | 0 |  |  | Durability & Reliability
|  | 2.1 | Earthquake Resistance, Seismic Isolation, Seismic Control, & Vibration Control | [11 empty] | 3 | 0.5 | 0 | 0 |  |  |  | 3 | 0.5 | 0 | 0 |  | 0.5 | 0 |  |  | Earthquake Resistance, Seismic Isolation, Seismic Control, & Vibration Control
|  |  | 1 | Earthquake-resistance |  |  | 0 | [7 empty] | 3 | 0.8 | 0 | 0 |  | 3 |  | 3 | 0.8 | 0 | 0 |  | 0.8 | 0 |  |  | Earthquake-resistance
|  |  | 2 | Seismic Isolation, Seismic & Vibration Control |  |  | 0 | [7 empty] | 3 | 0.2 | 0 | 0 |  | 3 |  | 3 | 0.2 | 0 | 0 |  | 0.2 | 0 |  |  | Seismic Isolation, Seismic & Vibration Control
|  | 2.2 | Service Life of Components | [11 empty] | 3 | 0.3 | 0 | 0 |  |  |  | 3 | 0.3 | 0 | 0 |  | 0.3 | 0 |  |  | Service Life of Components
|  |  | 1 | Service Life of Structural Materials |  |  | 0 | [7 empty] | 3 | 0.2 | 0 | 0 |  | 3 |  | 3 | 0.2 | 0 | 0 |  | 0.2 | 0 |  |  | Service Life of Structural Materials
|  |  | 2 | Necessary Refurbishment Interval for Exterior Finishes |  |  | 0 | [7 empty] | 3 | 0.2 | 0 | 0 |  | 3 |  | 3 | 0.2 | 0 | 0 |  | 0.2 | 0 |  |  | Necessary Refurbishment Interval for Exterior Finishes
|  |  | 3 | Necessary Renewal Interval for Main Interior Finishes |  |  | 0 | [7 empty] | 3 | 0.1 | 0 | 0 |  | 3 |  | 3 | 0.1 | 0 | 0 |  | 0.1 | 0 |  |  | Necessary Renewal Interval for Main Interior Finishes
|  |  | 4 | Necessary Renewal Interval for Air Conditioning and Ventilation Ducts |  |  | 0 | [7 empty] | 3 | 0.1 | 0 | 0 |  | 3 |  | 3 | 0.1 | 0 | 0 |  | 0.1 | 0 |  |  | Necessary Renewal Interval for Air Conditioning and Ventilation Ducts
|  |  | 5 | Necessary Renewal Interval for HVAC and Water Supply and Drainage Pipes |  |  | 0 | [7 empty] | 3 | 0.2 | 0 | 0 |  | 3 |  | 3 | 0.2 | 0 | 0 |  | 0.2 | 0 |  |  | Necessary Renewal Interval for HVAC and Water Supply and Drainage Pipes
|  |  | 6 | Necessary Replacement Interval for Major Equipment and Services |  |  | 0 | [7 empty] | 3 | 0.2 | 0 | 0 |  | 3 |  | 3 | 0.2 | 0 | 0 |  | 0.2 | 0 |  |  | Necessary Replacement Interval for Major Equipment and Services
|  | 2.3 | Appropriate renewal | [11 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | Appropriate Renewal
|  |  | 1 | [11 empty] | 3 | 0 | 0 | 0 |  | 3 |  | 3 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0
|  |  | 2 | [11 empty] | 3 | 0 | 0 | 0 |  | 3 |  | 3 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0
|  |  | 3 | [11 empty] | 3 | 0 | 0 | 0 |  | 3 |  | 3 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0
|  | 2.4 | Reliability | [11 empty] | 3 | 0.2 | 0 | 0 |  |  |  | 3 | 0.2 | 0 | 0 |  | 0.2 | 0 |  |  | Reliability
|  |  | 1 | HVAC System |  |  | 0 | [7 empty] | 3 | 0.2 | 0 | 0 |  | 3 |  | 3 | 0.2 | 0 | 0 |  | 0.2 | 0 |  |  | HVAC System
|  |  | 2 | Water Supply & Drainage |  |  | 0 | [7 empty] | 3 | 0.2 | 0 | 0 |  | 3 |  | 3 | 0.2 | 0 | 0 |  | 0.2 | 0 |  |  | Water Supply & Drainage
|  |  | 3 | Electrical Equipment |  |  | 0 | [7 empty] | 3 | 0.2 | 0 | 0 |  | 3 |  | 3 | 0.2 | 0 | 0 |  | 0.2 | 0 |  |  | Electrical Equipment
|  |  | 4 | Support Method of Machines & Ducts |  |  | 0 | [7 empty] | 3 | 0.2 | 0 | 0 |  | 3 |  | 3 | 0.2 | 0 | 0 |  | 0.2 | 0 |  |  | Support Method of Machines & Ducts
|  |  | 5 | Communications & IT Equipment |  |  | 0 | [7 empty] | 3 | 0.2 | 0 | 0 |  | 3 |  | 3 | 0.2 | 0 | 0 |  | 0.2 | 0 |  |  | Communications & IT Equipment
[15 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | 0 |  |  | 0
| 3 | Flexibility & Adaptability | [12 empty] | 3 | 0.3 | 0 | 0 | 3 |  |  | 3 | 0.3 | 0 | 0 | 3 | 0.3 | 0 |  |  | Flexibility & Adaptability
|  | 3.1 | Spatial Margin | [11 empty] | 3 | 0.3 | 0 | 0 |  |  |  | 3 | 0.3 | 0 | 0 |  | 0.3 | 0 |  |  | Spatial Margin
|  |  | 1 | Allowance for Floor-to-floor Height |  |  | 0 | [7 empty] | 3 | 0.6 | 0 | 0 |  | 3 | 3 | 3 | 0.6 | 0 | 0 |  | 0.6 | 0 |  |  | Allowance for Floor-to-floor Height
|  |  | 2 | Flexibility in Floor Layout |  |  | 0 | [7 empty] | 3 | 0.4 | 0 | 0 |  | 3 | 3 | 3 | 0.4 | 0 | 0 |  | 0.4 | 0 |  |  | Flexibility in Floor Layout
|  | 3.2 | Floor Load Margin |  |  |  | 0 | [7 empty] | 3 | 0.3 | 0 | 0 |  | 3 | 3 | 3 | 0.3 | 0 | 0 |  | 0.3 | 0 |  |  | Floor Load Margin
|  | 3.3 | System Renewability | [11 empty] | 3 | 0.4 | 0 | 0 |  |  |  | 3 | 0.4 | 0 | 0 |  | 0.4 | 0 |  |  | System Renewability
|  |  | 1 | Ease of Air Conditioning Duct Renewal |  |  | 0 | [7 empty] | 3 | 0.2 | 0 | 0 |  | 3 |  | 3 | 0.2 | 0 | 0 |  | 0.2 | 0 |  |  | Ease of Air Conditioning Duct Renewal
|  |  | 2 | Ease of Water Supply and Drain Pipe Renewal |  |  | 0 | [7 empty] | 3 | 0.2 | 0 | 0 |  | 3 |  | 3 | 0.2 | 0 | 0 |  | 0.2 | 0 |  |  | Ease of Water Supply and Drain Pipe Renewal
|  |  | 3 | Ease of Electrical Wiring Renewal |  |  | 0 | [7 empty] | 3 | 0.1 | 0 | 0 |  | 3 |  | 3 | 0.1 | 0 | 0 |  | 0.1 | 0 |  |  | Ease of Electrical Wiring Renewal
|  |  | 4 | Ease of Communications Cable Renewal |  |  | 0 | [7 empty] | 3 | 0.1 | 0 | 0 |  | 3 |  | 3 | 0.1 | 0 | 0 |  | 0.1 | 0 |  |  | Ease of Communications Cable Renewal
|  |  | 5 | Ease of Equipment Renewal |  |  | 0 | [7 empty] | 3 | 0.2 | 0 | 0 |  | 3 |  | 3 | 0.2 | 0 | 0 |  | 0.2 | 0 |  |  | Ease of Equipment Renewal
|  |  | 6 | Provision of Backup Space |  |  | 0 | [7 empty] | 3 | 0.2 | 0 | 0 |  | 3 |  | 3 | 0.2 | 0 | 0 |  | 0.2 | 0 |  |  | Provision of Backup Space
| Q3 Outdoor Environment on Site | [13 empty] | 0 | 0.3 | 0 | 0 | 3 |  |  |  | 0.3 |  |  | 3 | 0.3 | 0 | No.14 | No.15 | Outdoor Environment on Site
| 1 | Preservation & Creation of Biotope |  |  |  |  | 0 | [7 empty] | 3 | 0.3 | 0 | 0 | 3 | 3 |  | 3 | 0.3 | 0 | 0 | 3 | 0.3 | 0 |  |  | Preservation & Creation of Biotope
[15 empty] | 0 | 0 | 0 | 0 | 0 | 100 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
[15 empty] | 0 | 0 | 0 | 0 |  | 100 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0
| 2 | Townscape & Landscape |  |  |  |  | 0 | [7 empty] | 3 | 0.4 | 0 | 0 | 3 | 3 |  | 3 | 0.4 | 0 | 0 | 3 | 0.4 | 0 |  |  | Townscape & Landscape
| 3 | Local Characteristics & Outdoor Amenity | [12 empty] | 3 | 0.3 | 0 | 0 | 3 |  |  | 3 | 0.3 | 0 | 0 | 3 | 0.3 | 0 |  |  | Local Characteristics & Outdoor Amenity
|  | 3.1 | Attention to Local Character & Improvement of Comfort |  |  |  | 0 | [7 empty] | 3 | 0.5 | 0 | 0 |  | 3 |  | 3 | 0.5 | 0 | 0 |  | 0.5 | 0 |  |  | Attention to Local Character & Improvement of Comfort
|  | 3.2 | Improvement of the Thermal Environment on Site |  |  |  | 0 | [7 empty] | 3 | 0.5 | 0 | 0 |  | 3 |  | 3 | 0.5 | 0 | 0 |  | 0.5 | 0 |  |  | Improvement of the Thermal Environment on Site
[15 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | 0 |  |  | 0
| LR: Environmental Load Reduction of Building | [14 empty] | 0 |  | 0 | #VALUE! |  |  |  | 0 |  |  | #VALUE! | 0 | 0 |  |  | Environmental Load Reduction of Building
| LR1 Energy | Energy | [12 empty] | 0 | #VALUE! | 0 | 0 | 4 |  |  |  | #VALUE! |  |  | 4 | 0.4 | 0 | No.14 | No.15 | Energy
| 1 | Control of Heat Load on Building Envelopes |  |  |  |  | 0 | [7 empty] | 3 | 0.2 | 0 | 0 | 3 | 3 |  | 3 | 0.2 | 0 | 0 | 3 | 0.2 | 0 |  |  | Control of Heat Load on Building Envelopes
| 2 | Natural Energy Utilization (Direct Use) |  |  |  |  | 0 | [7 empty] | 3 | 0.1 | 0 | 0 | 3 | 3 |  | 3 | 0.1 | 0 | 0 | 3 | 0.1 | 0 |  |  | Natural Energy Utilization (Direct Use)
[15 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0
|  |  | 自然エネルギー利用 | [11 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0
[15 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0
[15 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0
| 3 | Efficiency in Building Service System |  |  |  |  | 0 | [7 empty] | 5 | 0.5 | 0 | 0 | 5 | 5 |  | 5 | 0.5 | 0 | 0 | 5 | 0.5 | 0 |  |  | Efficiency in Building Service System
|  |  | Other than apartment | [11 empty] | 5 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 1 | 0 |  |  | Other than apartment
|  |  | Apartment | [11 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | Apartment
|  | 3.1 | 空調設備 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 | 0 |  |  | 0
|  | 3.2 | 換気設備 | [11 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | 0 |  |  | 0
|  | 3.3 | 照明設備 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 | 0 |  |  | 0
|  | 3.4 | 給湯設備 | [11 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | 0 |  |  | 0
|  | 3.5 | 昇降機設備 | [11 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | 0 |  |  | 0
|  | 3.6 | エネルギー利用効率化設備 | [11 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 0 |  | 0 |  | 0 | 0 |  |  | 0
| 4 | Initiatives for Efficient Operation | [12 empty] | 3 | 0.2 | 0 | 0 | 3 |  |  | 3 | 0.2 | 0 | 0 | 3 | 0.2 | 0 |  |  | Initiatives for Efficient Operation
|  |  | Other than apartments | [11 empty] | 3 | 1 | 0 | 0 |  |  |  | 3 | 1 | 0 | 0 |  | 1 | 0 |  |  | Other than apartments
|  |  | 4.1 | Monitoring |  |  | 0 | [7 empty] | 3 | 0.4 | 0 | 0 |  | 3 |  | 3 | 0.4 | 0 | 0 |  | 0.4 |  |  |  | Monitoring
|  |  | 4.2 | Operation & Management System |  |  | 0 | [7 empty] | 3 | 0.4 | 0 | 0 |  | 3 |  | 3 | 0.4 | 0 | 0 |  | 0.4 |  |  |  | Operation & Management System
|  |  | 4.3 | Expanding adoption of non-fossil energy |  |  | 0 | [7 empty] | 3 | 0.1 | 0 | 0 |  | 3 |  | 3 | 0.1 | 0 | 0 |  | 0.1 |  |  |  | Expanding adoption of non-fossil energy
|  |  | 4.4 | Promoting Commissioning |  |  | 0 | [7 empty] | 3 | 0.1 | 0 | 0 |  | 3 |  | 3 | 0.1 | 0 | 0 |  | 0.1 |  |  |  | Promoting Commissioning
|  |  | Apartments | [11 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | Apartments
|  |  | 4.1 | Monitoring |  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 |  | 3 |  | 0 | 0 | 0 | 0 |  | 0 |  |  |  | Monitoring
|  |  | 4.2 | Operation & Management System |  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 |  | 3 |  | 0 | 0 | 0 | 0 |  | 0 |  |  |  | Operation & Management System
| LR2 Resources & Materials | [13 empty] | 0 | #VALUE! | 0 | 0 | 3 |  |  |  | #VALUE! |  |  | 3 | 0.3 | 0 | No.14 | No.15 | Resources & Materials
| 1 | Water Resources | [12 empty] | 3 | 0.2 | 0 | 0 | 3 |  |  | 3 | 0.2 | 0 | 0 | 3 | 0.2 | 0 |  |  | Water Resources
|  | 1.1 | Water Saving |  |  |  | 0 | [7 empty] | 3 | 0.4 | 0 | 0 |  | 3 |  | 3 | 0.4 | 0 | 0 |  | 0.4 | 0 |  |  | Water Saving
|  | 1.2 | Rain Water & Waste Water Use | [11 empty] | 3 | 0.6 | 0 | 0 |  |  |  | 3 | 0.6 | 0 | 0 |  | 0.6 | 0 |  |  | Rain Water & Waste Water Use
|  |  | 1 | Rainwater Use System |  |  | 0 | [7 empty] | 3 | 0.7 | 0 | 0 |  | 3 |  | 3 | 0.7 | 0 | 0 |  | 0.7 | 0 |  |  | Rainwater Use System
|  |  | 2 | Waste Water Reuse System |  |  | 0 | [7 empty] | 3 | 0.3 | 0 | 0 |  | 3 |  | 3 | 0.3 | 0 | 0 |  | 0.3 | 0 |  |  | Waste Water Reuse System
| 2 | Reducing Use of Non-renewable Resources | [12 empty] | 3 | 0.6 | 0 | 0 | 3 |  |  | 3 | 0.6 | 0 | 0 | 3 | 0.6 | 0 |  |  | Reducing Use of Non-renewable Resources
|  | 2.1 | Reducing Use of Materials |  |  |  | 0 | [7 empty] | 3 | 0.1 | 0 | 0 |  | 3 |  | 3 | 0.1 | 0 | 0 |  | 0.1 | 0 |  |  | Reducing Use of Materials
|  | 2.2 | Continuing Use of Existing Structural Frame, etc. |  |  |  | 0 | [7 empty] | 3 | 0.2 | 0 | 0 |  | 3 |  | 3 | 0.2 | 0 | 0 |  | 0.2 | 0 |  |  | Continuing Use of Existing Structural Frame, etc.
|  | 2.3 | Use of Recycled Materials as Structural Materials |  |  |  | 0 | [7 empty] | 3 | 0.2 | 0 | 0 |  | 3 |  | 3 | 0.2 | 0 | 0 |  | 0.2 | 0 |  |  | Use of Recycled Materials as Structural Materials
|  | 2.4 | Use of Recycled Materials as Non-structural Materials |  |  |  | 0 | [7 empty] | 3 | 0.2 | 0 | 0 |  | 3 |  | 3 | 0.2 | 0 | 0 |  | 0.2 | 0 |  |  | Use of Recycled Materials as Non-structural Materials
|  | 2.5 | Timber from Sustainable Forestry |  |  |  | 0 | [7 empty] | 3 | 0.1 | 0 | 0 |  | 3 |  | 3 | 0.1 | 0 | 0 |  | 0.1 | 0 |  |  | Timber from Sustainable Forestry
|  | 2.6 | Reusability of Components and Materials |  |  |  | 0 | [7 empty] | 3 | 0.2 | 0 | 0 |  | 3 |  | 3 | 0.2 | 0 | 0 |  | 0.2 | 0 |  |  | Reusability of Components and Materials
|  | 2.6 | 部材の再利用可能性向上への取組み | [11 empty] | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0
|  |  | 1 | 躯体のリサイクル・リユース | [10 empty] | 5 | 0 | 0 | 0 |  | 5 |  | 5 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0
|  |  | 2 | 屋根材のリサイクル・リユース | [10 empty] | 4 | 0 | 0 | 0 |  | 4 |  | 4 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0
|  |  | 3 | 外壁材のリサイクル・リユース | [10 empty] | 4 | 0 | 0 | 0 |  | 4 |  | 4 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0
|  |  | 4 | 内装材のリサイクル・リユース | [10 empty] | 4 | 0 | 0 | 0 |  | 4 |  | 4 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0
|  |  | 5 | 設備機器のリサイクル・リユース | [10 empty] | 1 | 0 | 0 | 0 |  | 1 |  | 1 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0
|  |  | 6 | 外構資材のリユース | [10 empty] | 1 | 0 | 0 | 0 |  | 1 |  | 1 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0
|  | 2.7 | 廃棄物発生量の最小化 | [11 empty] | 2 | 0 | 0 | 0 |  | 2 |  | 2 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0
| 3 | Avoiding the Use of Materials with Pollutant Content | [12 empty] | 3 | 0.2 | 0 | 0 | 3 |  |  | 3 | 0.2 | 0 | 0 | 3 | 0.2 | 0 |  |  | Avoiding the Use of Materials with Pollutant Content
|  | 3.1 | Use of Materials without Harmful Substances |  |  |  | 0 | [7 empty] | 3 | 0.3 | 0 | 0 |  | 3 |  | 3 | 0.3 | 0 | 0 |  | 0.3 | 0 |  |  | Use of Materials without Harmful Substances
|  | 3.2 | Avoidance of CFCs and Halons | [11 empty] | 3 | 0.7 | 0 | 0 |  |  |  | 3 | 0.7 | 0 | 0 |  | 0.7 | 0 |  |  | Avoidance of CFCs and Halons
|  |  | 1 | Fire Retardant |  |  | 0 | [7 empty] | 2 | 0.33333 | 0 | 0 |  | 2 |  | 2 | 0.33333 | 0 | 0 |  | 0.33333 | 0 |  |  | Fire Retardant
|  |  | 2 | Foaming Agents (Insulation Materials, etc.) |  |  | 0 | [7 empty] | 3 | 0.33333 | 0 | 0 |  | 3 |  | 3 | 0.33333 | 0 | 0 |  | 0.33333 | 0 |  |  | Foaming Agents (Insulation Materials, etc.)
|  |  | 3 | Refrigerants |  |  | 0 | [7 empty] | 4 | 0.33333 | 0 | 0 |  | 4 |  | 4 | 0.33333 | 0 | 0 |  | 0.33333 | 0 |  |  | Refrigerants
| LR3 Off-site Environment | [13 empty] | 0 | #VALUE! | 0 | 0 | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE! | 0.3 | 0 | No.14 | No.15 | Off-site Environment
| 1 | Consideration of Global Warming |  |  |  |  | 0 | [7 empty] | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! |  | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | 0.33333 | 0 |  |  | Consideration of Global Warming
| 2 | Consideration of Local Environment | [12 empty] | 3 | #VALUE! | 0 | 0 | 3 |  |  | 3 | #VALUE! | 0 | 0 | 3 | 0.33333 | 0 |  |  | Consideration of Local Environment
|  | 2.1 | Air Pollution |  |  |  | 0 | [7 empty] | 3 | 0.25 | 0 | 0 |  | 3 |  | 3 | 0.25 | 0 | 0 |  | 0.25 | 0 |  |  | Air Pollution
|  | 2.2 | Heat Island Effect |  |  |  | 0 | [7 empty] | 3 | 0.5 | 0 | 0 |  | 3 |  | 3 | 0.5 | 0 | 0 |  | 0.5 | 0 |  |  | Heat Island Effect
|  | 2.3 | Load on Local Infrastructure | [11 empty] | 3 | 0.25 | 0 | 0 |  |  |  | 3 | 0.25 | 0 | 0 |  | 0.25 | 0 |  |  | Load on Local Infrastructure
|  |  | 1 | Reduction of Rainwater Discharge Loads |  |  | 0 | [7 empty] | 3 | 0.25 | 0 | 0 |  | 3 |  | 3 | 0.25 | 0 | 0 |  | 0.25 | 0 |  |  | Reduction of Rainwater Discharge Loads
|  |  | 2 | Sewage Load Suppression |  |  | 0 | [7 empty] | 3 | 0.25 | 0 | 0 |  | 3 |  | 3 | 0.25 | 0 | 0 |  | 0.25 | 0 |  |  | Sewage Load Suppression
|  |  | 3 | Traffic Load Control |  |  | 0 | [7 empty] | 3 | 0.25 | 0 | 0 |  | 3 |  | 3 | 0.25 | 0 | 0 |  | 0.25 | 0 |  |  | Traffic Load Control
|  |  | 4 | Reduction of Waste Treatment Loads |  |  | 0 | [7 empty] | 3 | 0.25 | 0 | 0 |  | 3 |  | 3 | 0.25 | 0 | 0 |  | 0.25 | 0 |  |  | Reduction of Waste Treatment Loads
|  | 2.1 | 廃棄物処理負荷抑制 | [11 empty] | 100 | 0 | 0 | 0 |  | 100 |  | 100 | 0 | 0 | 0 |  | 0 |  |  |  | 0
| 3 | Consideration of Surrounding Environment | [12 empty] | 3 | #VALUE! | 0 | 0 | 3 |  |  | 3 | #VALUE! | 0 | 0 | 3 | 0.33333 | 0 |  |  | Consideration of Surrounding Environment
|  | 3.1 | Noise, Vibration & Odor | [11 empty] | 3 | 0.4 | 0 | 0 |  |  |  | 3 | 0.4 | 0 | 0 |  | 0.4 | 0 |  |  | Noise, Vibration & Odor
|  |  | 1 | Noise |  |  | 0 | [7 empty] | 3 | 0.33333 | 0 | 0 |  | 3 |  | 3 | 0.33333 | 0 | 0 |  | 0.33333 | 0 |  |  | Noise
|  |  | 2 | Vibration |  |  | 0 | [7 empty] | 3 | 0.33333 | 0 | 0 |  | 3 |  | 3 | 0.33333 | 0 | 0 |  | 0.33333 | 0 |  |  | Vibration
|  |  | 3 | Odor |  |  | 0 | [7 empty] | 3 | 0.33333 | 0 | 0 |  | 3 |  | 3 | 0.33333 | 0 | 0 |  | 0.33333 | 0 |  |  | Odor
|  | 3.2 | Wind/Sand Damage & Sunlight Obstruction | [11 empty] | 3 | 0.4 | 0 | 0 |  |  |  | 3 | 0.4 | 0 | 0 |  | 0.4 | 0 |  |  | Wind/Sand Damage & Sunlight Obstruction
|  |  | 1 | Restriction of Wind Damage |  |  | 0 | [7 empty] | 3 | 0.7 | 0 | 0 |  | 3 |  | 3 | 0.7 | 0 | 0 |  | 0.7 | 0 |  |  | Restriction of Wind Damage
|  |  | 2 | Control of Sand and Dust |  |  | 0 | [7 empty] | 0 | 0 | 0 |  |  | 3 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | Control of Sand and Dust
|  |  | 3 | Restriction of sunlight obstruction |  |  | 0 | [7 empty] | 3 | 0.3 | 0 | 0 |  | 3 |  | 3 | 0.3 | 0 | 0 |  | 0.3 | 0 |  |  | Restriction of Sunlight Obstruction
|  | 3.3 | Light Pollution | [11 empty] | 3 | 0.2 | 0 | 0 |  |  |  | 3 | 0.2 | 0 | 0 |  | 0.2 | 0 |  |  | Light Pollution
|  |  | 1 | Outdoor Illumination and Light that Spills from Interiors |  |  | 0 | [7 empty] | 3 | 0.7 | 0 | 0 |  | 3 |  | 3 | 0.7 | 0 | 0 |  | 0.7 | 0 |  |  | Outdoor Illumination and Light that Spills from Interiors
|  |  | 2 | Measures for Reflected Solar Glare from Building Walls |  |  | 0 | [7 empty] | 3 | 0.3 | 0 | 0 |  | 3 |  | 3 | 0.3 | 0 | 0 |  | 0.3 | 0 |  |  | Measures for Reflected Solar Glare from Building Walls
| CASBEE for Building Design (New Construction) 2024 Edition | [17 empty] | XXX Building
| Efforts to be evaluated |  |  |  | Total | Total 2 | No.1 | No.2 | No.3 | No.4 | No.5 | No.6 | No.7 | No.8 | No.9 | No.10 | No.11 | No.12 | No.13
| Q1 | Indoor Environment |  |  | 合計 |  | No.1 | No.2 | No.3 | No.4 | No.5 | No.6 | No.7 | No.8 | No.9 | No.10 | No.11 | No.12 | No.13
| 1 | Sound Environment
| 1.1 | Indoor Noise Level
| 1.1.1 | Background noise level
| 1.1.2 | Equipment noise
| 1.2 | Sound Insulation
| 1.2.1 | Sound Insulation of Openings
| 1.2.2 | Sound Insulation of Partition Walls
| 1.2.3 | Sound Insulation Performance of Floor Slabs (light-weight impact source)
| 1.2.4 | Sound Insulation Performance of Floor Slabs (heavy-weight impact source)
| 1.3 | Sound Absorption
| 2 | Thermal Comfort
| 2.1 | Room Temperature Control
| 2.1.1 | Room Temperature
| 2.1.2 | Variable Loads and Following-up Control
| 2.1.2 | Perimeter Performance
| 2.1.3 | Zoned Control
| 2.1.5 | Temperature and Humidity Control
| 2.1.6 | Individual Control
| 2.1.7 | Allowance for After-hours Air Conditioning
| 2.1.8 | Monitoring Systems
| 2.2 | Humidity Control
| 2.3 | Type of Air Conditioning System
| 2.3 | 0
| 2.3.1 | 0
| 2.3.2 | 0
| 3 | Lighting & Illumination
| 3.1 | Daylighting
| 3.1.1 | Daylight Factor
| 3.1.2 | Openings by Orientation
| 3.1.3 | Daylight Devices
| 3.2 | Anti-glare Measures
| 3.2.1 | Glare from Light Fixtures
| 3.2.1 | Daylight Control
| 3.2.3 | Reflection Control
| 3.3 | Illuminance Level
| 3.3.1 | 照度
| 3.3.2 | 照度均斉度
| 3.4 | Lighting Controllability
| 4 | Air Quality
| 4.1 | Source Control
| 4.1.1 | Chemical Pollutants
| 4.1.2 | Asbestos
| 4.1.3 | Mites, Mold etc.
| 4.1.4 | Legionella
| 4.2 | Ventilation
| 4.2.1 | Ventilation Rate
| 4.2.2 | Natural Ventilation Performance
| 4.2.3 | Consideration for Outside Air Intake
| 4.2.4 | Air Supply Planning
| 4.3 | Operation Plan
| 4.3.1 | CO2 Monitoring
| 4.3.2 | Control of Smoking
| Q2 | Quality of Service
| 1 | Service Ability
| 1.1 | Functionality & Usability
| 1.1.1 | Provision of Space & Storage
| 1.1.2 | Use of Advanced Information System
| 1.1.3 | Barrier-free Planning
| 1.2 | Amenity
| 1.2.1 | Perceived Spaciousness & Access to View
| 0 | 0
| 1.2.2 | Space for Refreshment
| 1.2.3 | Décor Planning |  |  | 2 | 0 | No.1 No.1: Yes; No.3 No.3: Yes; No.4 No.4: 0; No.5 No.5: 0; No.6 No.6: 0; No.7 No.7: 0; No.8 No.8: 0
| 0 | 0
| 1.3 | Maintenance Management
| 1.3.1 | Design that Considers Maintenance Management |  |  | 4 |  | Yes | 0 | 0 | 0 | 0 | 0 | Yes | Yes | 0 | Yes | 0 | 0 | 0
| 1.3.2 | Securing Maintenance Management Functions |  |  | 6 |  | 0 | Yes | Yes | Yes | Yes | 0 | 0 | Yes | Yes | 0 | 0 | 0 | 0
| 1.3.3 | Sanitation management operations |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | Durability & Reliability
| 2.1 | Earthquake Resistance, Seismic Isolation, Seismic Control, & Vibration Control
| 2.1.1 | Earthquake-resistance
| 2.1.2 | Seismic Isolation, Seismic & Vibration Control
| 2.2 | Service Life of Components
| 2.2.1 | Service Life of Structural Materials
| 2.2.2 | Necessary Refurbishment Interval for Exterior Finishes
| 2.2.3 | Necessary Renewal Interval for Main Interior Finishes
| 2.2.4 | Necessary Renewal Interval for Air Conditioning and Ventilation Ducts
| 2.2.5 | Necessary Renewal Interval for HVAC and Water Supply and Drainage Pipes
| 2.2.6 | Necessary Replacement Interval for Major Equipment and Services
| 2.3 | Appropriate Renewal
| 2.3.1 | 0
| 2.3.2 | 0
| 2.3.3 | 0
| 2.4 | Reliability
| 2.4.1 | HVAC System |  |  | 1 |  | No.1 No.1: 0; No.2 No.2: Yes; No.3 No.3: 0; No.4 No.4: 0; No.5 No.5: 0
| 2.4.2 | Water Supply & Drainage |  |  | 2 | 1 | No.1 No.1: Yes; No.2 No.2: 0; No.3 No.3: 0; No.4 No.4: 0; No.5 No.5: 0; No.6 No.6: Yes; No.7 No.7: 0
| 2.4.3 | Electrical Equipment |  |  | 2 | 2 | No.1 No.1: 0; No.2 No.2: 0; No.3 No.3: Yes; No.4 No.4: 0; No.5 No.5: Yes; No.6 No.6: 0
| 2.4.4 | Support Method of Machines & Ducts | bar: No.7 No.7 to XXX Building No.13 No.13
| 2.4.5 | Communications & IT Equipment |  |  | 2 |  | No.1 No.1: 0; No.2 No.2: Yes; No.3 No.3: 0; No.4 No.4: Yes; No.5 No.5: 0; No.6 No.6: 0
| 0 | 0
| 3 | Flexibility & Adaptability
| 3.1 | Spatial Margin
| 3.1.1 | Allowance for Floor-to-floor Height
| 3.1.2 | Flexibility in Floor Layout
| 3.2 | Floor Load Margin
| 3.3 | System Renewability
| 3.3.1 | Ease of Air Conditioning Duct Renewal
| 3.3.2 | Ease of Water Supply and Drain Pipe Renewal
| 3.3.3 | Ease of Electrical Wiring Renewal
| 3.3.4 | Ease of Communications Cable Renewal
| 3.3.5 | Ease of Equipment Renewal
| 3.3.6 | Provision of Backup Space
| Q3 | Outdoor Environment on Site
| 1 | Preservation & Creation of Biotope |  |  | 7 |  | 0 | 2 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 0
| 1 | 0 | bar: No.12 No.12 to XXX Building No.13 No.13
| 1.1 | 0 | bar: No.12 No.12 to XXX Building No.13 No.13
| 2 | Townscape & Landscape |  |  | 3 |  | No.1 No.1: 2; No.2 No.2: 1; No.3 No.3: 0; No.4 No.4: 0; No.5 No.5: 0; No.6 No.6: 0
| 3 | Local Characteristics & Outdoor Amenity | bar: No.12 No.12 to XXX Building No.13 No.13
| 3.1 | Attention to Local Character & Improvement of Comfort |  |  | 2 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0
| 3.2 | Improvement of the Thermal Environment on Site |  |  | 6 |  | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0
| 0 | 0
| LR | Environmental Load Reduction of Building
| LR1 | Energy
| 1 | Control of Heat Load on Building Envelopes
| 2 | Natural Energy Utilization (Direct Use) |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0
| 0 | 0
| 2.1 | 0
| 2.2 | 0
| 3 | Efficiency in Building Service System
| 3.1 | Other than apartment
| 3.2 | Apartment
| 3.1 | 0
| 3.2 | 0
| 3.3 | 0
| 3.4 | 0
| 3.5 | 0
| 0 | 0
| 4 | Initiatives for Efficient Operation
| 4.1 | Other than apartments
| 4.1.1 | Monitoring
| 4.1.2 | Operation & Management System
| 4.1.3 | Expanding adoption of non-fossil energy
| 4.1.4 | Promoting Commissioning |  |  | 1 |  | No.1 No.1: Yes; No.2 No.2: 0; No.3 No.3: 0; No.4 No.4: Yes; No.5 No.5: 0
| 4.2 | Apartments
| 4.2.1 | Monitoring
| 4.2.2 | Operation & Management System
| LR2 | Resources & Materials
| 1 | Water Resources
| 1.1 | Water Saving
| 1.2 | Rain Water & Waste Water Use
| 1.2.1 | Rainwater Use System
| 1.2.2 | Waste Water Reuse System |  |  |  |  | - | 0 | 0 | 0 | 0 | - | 0 | 0
| 2 | Reducing Use of Non-renewable Resources | bar: No.4 No.4 to XXX Building No.13 No.13
| 2.1 | Reducing Use of Materials |  |  | 2 |  | No.1 No.1: 1; No.2 No.2: 1; No.3 No.3: 0
| 2.2 | Continuing Use of Existing Structural Frame, etc. | bar: No.5 No.5 to XXX Building No.13 No.13
| 2.3 | Use of Recycled Materials as Structural Materials |  |  |  |  | No.1 No.1: 0; No.2 No.2: 0; No.3 No.3: 0; No.4 No.4: 0; No.5 No.5: 0
| 2.4 | Use of Recycled Materials as Non-structural Materials | bar: No.5 No.5 to XXX Building No.13 No.13
| 2.5 | Timber from Sustainable Forestry | bar: No.5 No.5 to XXX Building No.13 No.13
| 2.6 | Reusability of Components and Materials |  |  | 0 |  | No.1 No.1: 0; No.2 No.2: 0; No.3 No.3: 0; No.4 No.4: 0
| 2.6 | 0 | bar: No.5 No.5 to XXX Building No.13 No.13
| 2.6.1 | 0 | bar: No.5 No.5 to XXX Building No.13 No.13
| 2.6.2 | 0 | bar: No.5 No.5 to XXX Building No.13 No.13
| 2.6.3 | 0 | bar: No.5 No.5 to XXX Building No.13 No.13
| 2.6.4 | 0 | bar: No.5 No.5 to XXX Building No.13 No.13
| 2.6.5 | 0 | bar: No.5 No.5 to XXX Building No.13 No.13
| 2.6.6 | 0 | bar: No.5 No.5 to XXX Building No.13 No.13
| 2.7 | 0 | bar: No.5 No.5 to XXX Building No.13 No.13
| 3 | Avoiding the Use of Materials with Pollutant Content | bar: No.5 No.5 to XXX Building No.13 No.13
| 3.1 | Use of Materials without Harmful Substances |  |  | 0
| 3.2 | Avoidance of CFCs and Halons
| 3.2.1 | Fire Retardant
| 3.2.2 | Foaming Agents (Insulation Materials, etc.)
| 3.2.3 | Refrigerants
| LR3 | Off-site Environment
| 1 | Consideration of Global Warming
| 2 | Consideration of Local Environment
| 2.1 | Air Pollution
| 2.2 | Heat Island Effect |  |  | 6 |  | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0
| 2.3 | Load on Local Infrastructure
| 2.3.1 | Reduction of Rainwater Discharge Loads
| 2.3.2 | Sewage Load Suppression
| 2.3.3 | Traffic Load Control |  |  | 2 |  | No.1 No.1: 0; No.2 No.2: 1; No.3 No.3: 0; No.4 No.4: 1; No.5 No.5: 0; No.6 No.6: 0
| 2.3.4 | Reduction of Waste Treatment Loads |  |  | 3 |  | No.1 No.1: 1; No.2 No.2: 1; No.3 No.3: 0; No.4 No.4: 0; No.6 No.6: 1; No.7 No.7: 0
| 0 | 0 | bar: No.8 No.8 to XXX Building No.13 No.13
| 3 | Consideration of Surrounding Environment | bar: No.8 No.8 to XXX Building No.13 No.13
| 3.1 | Noise, Vibration & Odor | bar: No.8 No.8 to XXX Building No.13 No.13
| 3.1.1 | Noise | bar: No.8 No.8 to XXX Building No.13 No.13
| 3.1.2 | Vibration | bar: No.8 No.8 to XXX Building No.13 No.13
| 3.1.3 | Odor | bar: No.8 No.8 to XXX Building No.13 No.13
| 3.2 | Wind/Sand Damage & Sunlight Obstruction | bar: No.8 No.8 to XXX Building No.13 No.13
| 3.2.1 | Restriction of Wind Damage | bar: No.8 No.8 to XXX Building No.13 No.13
| 3.2.2 | Control of Sand and Dust |  |  | 2 |  | No.1 No.1: 2; No.2 No.2: 0
| 3.2.3 | Restriction of Sunlight Obstruction | bar: No.3 No.3 to XXX Building No.13 No.13
| 3.3 | Light Pollution | bar: No.3 No.3 to XXX Building No.13 No.13
| 3.3.1 | Outdoor Illumination and Light that Spills from Interiors |  |  | 2 |  | No.1 No.1: 0; No.2 No.2: 2
| 3.3.2 | Measures for Reflected Solar Glare from Building Walls
Key indicators
| Q1 | Indoor Environment
| 1 | Sound Environment
| 1.1 | Indoor Noise Level
| 1.1.1 | Background noise level
| 1.1.2 | Equipment noise
| 1.2 | Sound Insulation
| 1.2.1 | Sound Insulation of Openings
| 1.2.2 | Sound Insulation of Partition Walls
| 1.2.3 | Sound Insulation Performance of Floor Slabs (light-weight impact source)
| 1.2.4 | Sound Insulation Performance of Floor Slabs (heavy-weight impact source)
| 1.3 | Sound Absorption
| 2 | Thermal Comfort
| 2.1 | Room Temperature Control
| 2.1.1 | Room Temperature
| 2.1.2 | Variable Loads and Following-up Control
| 2.1.2 | Perimeter Performance |  |  |  |  | No.1 No.1: Window system SC; No.3 No.3: 0; No.4 No.4: window solar heat gain coef(η); No.7 No.7: 0
[7 empty] | U value |  |  | window system | 0 | roof | 0 | outer walls | 0 | floor | 0 | [W/m2K]
[7 empty] | Dwelling area: | Window system U value |  | 0 | perimeter UA value |  | 0 | ηAC | 0 | ηAH | 0
| 2.1.6 | Individual Control
| 2.1.7 | Allowance for After-hours Air Conditioning
| 2.1.8 | Monitoring Systems
| 2.2 | Humidity Control
| 2.3 | Type of Air Conditioning System
| 2.3 | 0
| 2.3.1 | 0
| 2.3.2 | 0
| 3 | Lighting & Illumination
| 3.1 | Daylighting
| 3.1.1 | Daylight Factor |  |  |  |  | No.1 No.1: Daylight factor; No.3 No.3: 0%
| 3.1.2 | Openings by Orientation
| 3.1.3 | Daylight Devices
| 3.2 | Anti-glare Measures
| 3.2.1 | Glare from Light Fixtures
| 3.2.1 | Daylight Control
| 3.2.3 | Reflection Control
| 3.3 | Illuminance Level
| 3.3.1 | 照度
| 3.3.2 | 照度均斉度
| 3.4 | Lighting Controllability
| 4 | Air Quality
| 4.1 | Source Control
| 4.1.1 | Chemical Pollutants
| 4.1.2 | Asbestos
| 4.1.3 | Mites, Mold etc.
| 4.1.4 | Legionella
| 4.2 | Ventilation
| 4.2.1 | Ventilation Rate
| 4.2.2 | Natural Ventilation Performance |  |  |  |  | No.1 No.1: Valid opening area for natural ventilation; No.4 No.4: 0%
| 4.2.3 | Consideration for Outside Air Intake
| 4.2.4 | Air Supply Planning
| 4.3 | Operation Plan
| 4.3.1 | CO2 Monitoring
| 4.3.2 | Control of Smoking
| Q2 | Quality of Service
| 1 | Service Ability
| 1.1 | Functionality & Usability
| 1.1.1 | Provision of Space & Storage |  |  |  |  | Working space |  | 0 | /person | Bedroom | 0 | /bed | Single room | 0 | Twin room | 0
| 1.1.2 | Use of Advanced Information System |  |  |  |  | No.1 No.1: Socket capacity; No.3 No.3: 0; No.4 No.4: VA/㎡
| 1.1.3 | Barrier-free Planning
| 1.2 | Amenity
| 1.2.1 | Perceived Spaciousness & Access to View |  |  |  |  | No.1 No.1: Celling height; No.3 No.3: 0; No.4 No.4: m
| 0 | 0
| 1.2.2 | Space for Refreshment |  |  |  |  | No.1 No.1: Refreshment space; No.4 No.4: 0%; No.6 No.6: Rest space; No.7 No.7: 0%
| 1.2.3 | Décor Planning
| 0 | 0
| 1.3 | Maintenance Management
| 1.3.1 | Design that Considers Maintenance Management
| 1.3.2 | Securing Maintenance Management Functions
| 1.3.3 | Sanitation management operations
| 2 | Durability & Reliability
| 2.1 | Earthquake Resistance, Seismic Isolation, Seismic Control, & Vibration Control
| 2.1.1 | Earthquake-resistance
| 2.1.2 | Seismic Isolation, Seismic & Vibration Control
| 2.2 | Service Life of Components
| 2.2.1 | Service Life of Structural Materials |  |  |  |  | No.1 No.1: Expected lifespan; No.3 No.3: 0; No.4 No.4: yr.
| 2.2.2 | Necessary Refurbishment Interval for Exterior Finishes |  |  |  |  | No.1 No.1: Expected necessary interval; No.3 No.3: 0; No.4 No.4: years
| 2.2.3 | Necessary Renewal Interval for Main Interior Finishes |  |  |  |  | No.1 No.1: Expected necessary interval; No.3 No.3: 0; No.4 No.4: years
| 2.2.4 | Necessary Renewal Interval for Air Conditioning and Ventilation Ducts
| 2.2.5 | Necessary Renewal Interval for HVAC and Water Supply and Drainage Pipes
| 2.2.6 | Necessary Replacement Interval for Major Equipment and Services |  |  |  |  | No.1 No.1: Expected necessary interval; No.3 No.3: 0; No.4 No.4: years
| 2.3 | Appropriate Renewal
| 2.3.1 | 0
| 2.3.2 | 0
| 2.3.3 | 0
| 2.4 | Reliability
| 2.4.1 | HVAC System
| 2.4.2 | Water Supply & Drainage
| 2.4.3 | Electrical Equipment
| 2.4.4 | Support Method of Machines & Ducts
| 2.4.5 | Communications & IT Equipment
| 0 | 0
| 3 | Flexibility & Adaptability
| 3.1 | Spatial Margin
| 3.1.1 | Allowance for Floor-to-floor Height |  |  |  |  | No.1 No.1: Floor height; No.3 No.3: 0; No.4 No.4: m
| 3.1.2 | Flexibility in Floor Layout |  |  |  |  | No.1 No.1: Wall length/area ratio; No.3 No.3: 0
| 3.2 | Floor Load Margin |  |  |  |  | No.1 No.1: Floor Load; No.3 No.3: 0; No.4 No.4: N/m2
| 3.3 | System Renewability
| 3.3.1 | Ease of Air Conditioning Duct Renewal
| 3.3.2 | Ease of Water Supply and Drain Pipe Renewal
| 3.3.3 | Ease of Electrical Wiring Renewal
| 3.3.4 | Ease of Communications Cable Renewal
| 3.3.5 | Ease of Equipment Renewal
| 3.3.6 | Provision of Backup Space
| Q3 | Outdoor Environment on Site
| 1 | Preservation & Creation of Biotope |  |  |  |  | No.1 No.1: Exterior Planting Index; No.3 No.3: #DIV/0!; No.6 No.6: Building Planting Index; No.7 No.7: 0%
| 1 | 0
| 1.1 | 0
| 2 | Townscape & Landscape
| 3 | Local Characteristics & Outdoor Amenity
| 3.1 | Attention to Local Character & Improvement of Comfort
| 3.2 | Improvement of the Thermal Environment on Site |  |  |  |  | Open space | 0% | horizontal projection areas |  |  | 0% | appropriate ground surface |  | 0% |  | paved surface | 0%
| 0 | 0
| LR | Environmental Load Reduction of Building
| LR1 | Energy
| 1 | Control of Heat Load on Building Envelopes |  |  |  |  | No.1 No.1: BPI/BPIm;; No.3 No.3: 0.97; No.4 No.4: Housing Performance Indication Standard; No.7 No.7: Not applicable; No.8 No.8: equivalent
| 2 | Natural Energy Utilization (Direct Use) |  |  |  |  | No.1 No.1: % of impact; No.3 No.3: 0%; No.8 No.8: % of classrooms w/ adequate natural light; No.9 No.9: 0%; No.10 No.10: % of dwellings w/ adequate natural light; No.12 No.12: 0%
[14 empty] | % of classrooms w/ adequate ventilation | 0% | % of dwellings w/ adequate ventilation |  | 0%
| 0 | 0
| 2.1 | 0
| 2.2 | 0
| 3 | Efficiency in Building Service System |  |  |  |  | No.7 No.7: Solar power generation; No.8 No.8: 0; No.9 No.9: kW Solar heat; No.10 No.10: 0; No.11 No.11: kW Battery; No.12 No.12: 0
|  | Other than apartment |  |  |  |  | BEI/BEIm; |  | [BEI] [BEIm] | 0.25 | [BEI＊] [BEIm*] | 0.5 |  | [BEI+] | 0 | 〇〇kW installed in 〇〇 City, used 〇〇GJ/yr, etc.
|  | Apartment |  |  |  |  | No.1 No.1: BEI; No.3 No.3: with renewables; No.5 No.5: w/o; No.8 No.8: Evaluated based on specification std.; No.10 No.10: 0
| 3.1 | 0 |  |  |  |  | No.1 No.1: BEI/BEIm
| 3.2 | 0 |  |  |  |  | No.1 No.1: BEI/BEIm
| 3.3 | 0 |  |  |  |  | No.1 No.1: BEI/BEIm
| 3.4 | 0 |  |  |  |  | No.1 No.1: BEI/BEIm
| 3.5 | 0 |  |  |  |  | No.1 No.1: BEI/BEIm
| 0 | 0 |  |  |  |  | No.1 No.1: BEI/BEIm
| 4 | Initiatives for Efficient Operation
| 4.1 | Other than apartments
| 4.1.1 | Monitoring
| 4.1.2 | Operation & Management System
| 4.2 | Apartments
| 4.2.1 | Monitoring
| 4.2.2 | Operation & Management System
| LR2 | Resources & Materials
| 1 | Water Resources
| 1.1 | Water Saving
| 1.2 | Rain Water & Waste Water Use
| 1.2.1 | Rainwater Use System |  |  |  |  | No.1 No.1: Rain water usage rate; No.3 No.3: 0%
| 1.2.2 | Waste Water Reuse System
| 2 | Reducing Use of Non-renewable Resources
| 2.1 | Reducing Use of Materials
| 2.2 | Continuing Use of Existing Structural Frame, etc.
| 2.3 | Use of Recycled Materials as Structural Materials
| 2.4 | Use of Recycled Materials as Non-structural Materials |  |  |  |  | No.1 No.1: Designated green procurement items; No.3 No.3: 0; No.5 No.5: Eco Mark products; No.7 No.7: 0; No.8 No.8: Specific items designated by local governments, etc.; No.11 No.11: 0
| 2.5 | Timber from Sustainable Forestry |  |  |  |  | No.1 No.1: Proportion of timber used; No.3 No.3: 0%
| 2.6 | Reusability of Components and Materials
| 2.6 | 0
| 2.6.1 | 0
| 2.6.2 | 0
| 2.6.3 | 0
| 2.6.4 | 0
| 2.6.5 | 0
| 2.6.6 | 0
| 2.7 | 0
| 3 | Avoiding the Use of Materials with Pollutant Content
| 3.1 | Use of Materials without Harmful Substances
| 3.2 | Avoidance of CFCs and Halons
| 3.2.1 | Fire Retardant |  |  |  |  | No.1 No.1: ODP; No.7 No.7: GWP
| 3.2.2 | Foaming Agents (Insulation Materials, etc.) |  |  |  |  | No.1 No.1: ODP; No.7 No.7: GWP
| 3.2.3 | Refrigerants |  |  |  |  | No.1 No.1: ODP; No.7 No.7: GWP
| LR3 | Off-site Environment
| 1 | Consideration of Global Warming
| 2 | Consideration of Local Environment
| 2.1 | Air Pollution
| 2.2 | Heat Island Effect |  |  |  |  | No.1 No.1: Exposed area ratio; No.3 No.3: #DIV/0!; No.4 No.4: Building spacing index Rw; No.6 No.6: 0
| 2.3 | Load on Local Infrastructure
| 2.3.1 | Reduction of Rainwater Discharge Loads
| 2.3.2 | Sewage Load Suppression
| 2.3.3 | Traffic Load Control
| 2.3.4 | Reduction of Waste Treatment Loads
| 0 | 0
| 3 | Consideration of Surrounding Environment
| 3.1 | Noise, Vibration & Odor
| 3.1.1 | Noise
| 3.1.2 | Vibration
| 3.1.3 | Odor
| 3.2 | Wind/Sand Damage & Sunlight Obstruction
| 3.2.1 | Restriction of Wind Damage
| 3.2.2 | Control of Sand and Dust
| 3.2.3 | Restriction of Sunlight Obstruction
| 3.3 | Light Pollution
| 3.3.1 | Outdoor Illumination and Light that Spills from Interiors
| 3.3.2 | Measures for Reflected Solar Glare from Building Walls
[7 empty] | appropriate ground surface |  |  | 0% |  | appropriate roof top surface |  | #DIV/0! | appropriate exterior wall surface |  | #DIV/0!
[7 empty] | Exposed area Sb |  | 0 |  | Ws: Maximum width of the site perpendicular to the prevailing wind direction |  |  | 0 | m | Hb: Standard height | 0 | m
[7 empty] | green area | 0 | water surface | 0 | evaporative material covered area |  | 0 | high solar reflectance material covered area | 0 | retroreflective material covered area |  | 0

## Factor
Emission factor |  |  |  |  | Examples of published emission factors by electricity supplier (for calculating greenhouse gas emissions by specified emitters) - FY2022 results - (August 29, 2024)
GHG emission factor of electricity consumption (for Std. Calculation) |  |  |  | ※Set the factor used for reference value. | Emission factor per PPS and alterative factor based on Ordinance on Calculations of GHG Emissions |  |  |  |  | 0 | ←オプションボタン番号
| PPS / evidence, etc. | emission factor |  |  | [1] | Basic emission factors (options are examples) |  |  | ＜Ref.＞adjusted factors
| XXX | N.A. | t-CO2/kWh |  |  | Hokkaido Electric Power Co., Inc. | 0.000533 |  | 0.000535
| Note: Purchases of green electricity are evaluated on individual calculation, |  |  |  |  | Tohoku Electric Power Co., Inc. | 0.000477 |  | 0.00046 | ↓事業社名 | ↓排出係数
| so they cannot be set here. |  |  |  |  | TEPCO Energy Partner, Inc. | 0.000457 |  | 0.000376 | XXX | 0
(1) Using a designated emission factor: | [5 empty] | Chubu Electric Power Miraiz Co., Inc. | 0.000433 |  | 0.00044
| PPS / evidence, etc. | emission factor |  |  |  | Hokuriku Electric Power Co., Inc. | 0.000487 |  | 0.000499 | N.A.
| XXX |  | (t-CO2/kWh) |  |  | Kansai Electric Power Co., Inc. | 0.00036 |  | 0.00042
[6 empty] | Chugoku Electric Power Co., Inc. | 0.000537 |  | 0.000544
(2) Using emission factor based on the calculation method for GHG emissions as referred to in the Act on Promotion of Global Warming Countermeasures: | [5 empty] | Shikoku Electric Power Co., Inc. | 0.00037 |  | 0.000447
[6 empty] | Kyushu Electric Power Co., Inc. | 0.000407 |  | 0.000462
A. | Electricity supplied by power producers/suppliers (PPS) |  |  |  |  | Okinawa Electric Power Co., Inc. | 0.00071 |  | 0.000675
| 調整後 | #N/A |  |  |  | XXX Power Co., Inc. (Record in 2022) | XXX |  | XXX
| PPS | emission factor |  |  | For cases other than those listed above, enter the PPS name and emission factor below.
|  | #N/A | (t-CO2/kWh) |  |  | XXX Power Co., Inc. (Record in 2022) | XXX |  | XXX
[5 empty] | [2] | Alternative emission factor
B. | Other |  |  |  |  | Alternative coefficient value | 0.000429 | (t-CO2/kWh)
| PPS / evidence, etc. | emission factor
| XXX |  | (t-CO2/kWh)
C. | Alternative emission factor
| PPS / evidence, etc. | emission factor
| Alternative emission factor |  | (t-CO2/kWh)
(3) Other than above:
| PPS / evidence, etc. | emission factor
| XXX |  | (t-CO2/kWh)

## Q1
[11 empty] | n Building Name | XXX Building
|  |  |  | 1 | Level 1 | ■Level 1
|  |  |  | 2 | Level 2 | ■Level 2 |  |  | プルダウン選択肢 | <N.A.> | Yes | Not apply | Preliminary design stage
|  |  |  | 3 | Level 3 | ■Level 3 | [5 empty] | Apply | Execution design stage
|  |  |  | 4 | Level 4 | ■Level 4 | [6 empty] | Construction completion stage
|  |  |  | 5 | Level 5 | ■Level 5 |  |  |  |  | Yes |  | 0
|  |  |  | 0 | Level | Level |  |  |  |  | No
|  | Q1 Indoor Environment | [5 empty] | Select from pull-down menus or enter figures and comments. |  |  |  |  | Execution design stage
The outline of efforts for environment should be filled in short if the score exceeds Level 3. If there is a lot to write, describe it on the consideration sheet.
|  | 1 | Sound Environment
|  | 1.1 | Indoor Noise Level | [9 empty] | dB(A)
|  |  |  | Entire Building and Common Areas |  |  | Weighting coef.(default) = | 0.4 |  | Dwelling and Accommodation Areas |  | Weighting coef.(default) = | 0
|  |  |  | 3 | Off,Hal(O.D.),Fct,Hsp(Waiting Room), Htl,Apt | Sch(Univ.,etc...), Hal(Lib.), Hsp(Doctor’s Off.) | Rtl,Rst | Hal(oth.) | Sch (ES/JS/JHS) | 3 | Hsp,Htl,Apt
1 | 1 |  |  | Level 1 | 50 < [Background noise level] | 45 < [Background noise level] | 55 < [Background noise level] | 40 < [Background noise level] | 60 < [Background noise level] | Level 1 | 45 < [Background noise level]
2 | - |  |  | Level 2 | (No corresponding level) | (No corresponding level) | (No corresponding level) | (No corresponding level) | 50 < [Background noise level] ≦ 60 | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | 45 < [Background noise level] ≦ 50 | 40 < [Background noise level] ≦ 45 | 50 < [Background noise level] ≦ 55 | 35 < [Background noise level] ≦ 40 | 45 < [Background noise level] ≦ 50 | ■Level 3 | 40 < [Background noise level] ≦ 45
4 | 4 |  |  | Level 4 | 40 < [Background noise level] ≦ 45 | 35 < [Background noise level] ≦ 40 | 45 < [Background noise level] ≦ 50 | 30 < [Background noise level] ≦ 35 | 35 < [Background noise level] ≦ 45 | Level 4 | 35 < [Background noise level] ≦ 40
5 | 5 |  |  | Level 5 | [Background noise level] ≦ 40 | [Background noise level] ≦ 35 | [Background noise level] ≦ 45 | [Background noise level] ≦ 30 | [Background noise level] ≦ 35 | Level 5 | [Background noise level] ≦ 35
0 | 0 |  |  | Outline of env. efforts
Noise: Allowable indoor noise levels
|  |  |  | dB (A) | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60
|  |  |  | NC-NR | 10～15 | 15～20 | 20～25 | 25～30 | 30～35 | 35～40 | 40～45 | 45～50 | 50～55
|  |  |  | Intrusiveness | 20: Silent―――; 25: ―――――――――Very Quiet―――――――――; 40: ―Not significantly noticeable――――――; 50: Perceived noise―; 55: ――――――Noise cannot be ignored
|  |  |  | Impact on | 30: A whispering voice is audible from 5m away; 40: Possible from 10m apart; 50: Possible from 3m apart; 60: Loud conversation (3m)
|  |  |  | conversation | 40: Telephone use (normal); 45: ――――――; 50: Telephone use (bearable); 55: ――――――; 60: Telephone use (unbearable)
|  |  |  | Studios | Silent room | Announcement | Radio studio | Television studios | Mixing room | General offices
|  |  |  | Venues and halls | 25: studio
|  |  |  | Hospitals | 25: Music hall; 30: Theater (medium); 35: Stage theaters; 40: Movie theater; 50: Hotel lobbies
|  |  |  | Hotels and | 40: and planetarium
|  |  |  | residentials |  | Hearing test | Special sickrooms | Operating rooms and bedrooms | Examining room | Laboratories | Waiting rooms
|  |  |  | General offices | 25: room
|  |  |  | Public buildings | 35: Reading rooms; 40: Bedrooms; 45: Banquet halls; 50: Lobbies
|  |  |  | Schools and churches | 35: Executive rooms; 40: Reception rooms; 45: Meeting rooms; 60: Typing and accounting rooms
|  |  |  | Commercial buildings | 35: and large meeting rooms
Refer to Architectural Institute of Japan, Handbook of Building Environmental Design 1 - Environment, 1978. P13
|  |  |  | 1.1.2 設備騒音対策 | 35: <N.A.>
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 0; 40: Dwelling and Accommodation Areas; 55: Weighting coef.(default) =; 60: 0
|  |  |  | 0 | 事・Sch・Rtl・Rst・Hal・Hsp・Htl・Fct |  | 事・Sch・Rtl・Rst・Hal・Hsp・Htl・Fct（2000㎡未満） |  | 0 | Hsp・Htl | Hsp・Htl（2000㎡未満） | 住
|  |  |  | Level 1 | 騒音対策を行っていない（評価する取組みにおいてなんら取組みがない） |  | 騒音対策を行っていない（評価する取組みにおいてなんら取組みがない） |  | Level 1 | 騒音対策を行っていない（評価する取組みにおいてなんら取組みがない） | 騒音対策を行っていない（評価する取組みにおいてなんら取組みがない） | 騒音対策を行っていない（評価する取組みにおいてなんら取組みがない）
|  |  |  | Level 2 | 20: 若干の対策を行っている（評価する取組みにおいて2項目以上を採用）; 30: 若干の対策を行っている（評価する取組みにおいて1項目以上を採用）; 40: Level 2; 45: 若干の対策を行っている（評価する取組みにおいて2項目以上を採用）; 50: 若干の対策を行っている（評価する取組みにおいて1項目以上を採用）
|  |  |  | Level 3 | 対策を行っている（評価する取組みにおいて4項目以上を採用） |  | 対策を行っている（評価する取組みにおいて2項目以上を採用） |  | Level 3 | 対策を行っている（評価する取組みにおいて4項目以上を採用） | 対策を行っている（評価する取組みにおいて2項目以上を採用） | 対策を行っている（評価する取組みにおいて2～3項目以上を採用）
|  |  |  | Level 4 | 20: やや高度な対策を行っている（評価する取組みにおいて6項目以上を採用）; 30: やや高度な対策を行っている（評価する取組みにおいて3項目以上を採用）; 40: Level 4; 45: やや高度な対策を行っている（評価する取組みにおいて6項目以上を採用）; 50: やや高度な対策を行っている（評価する取組みにおいて3項目以上を採用）
|  |  |  | Level 5 | 高度な対策を行っている（評価する取組みにおいて全ての項目を採用） |  | 高度な対策を行っている（評価する取組みにおいて全ての項目を採用） |  | Level 5 | 高度な対策を行っている（評価する取組みにおいて全ての項目を採用） | 高度な対策を行っている（評価する取組みにおいて全ての項目を採用） | 高度な対策を行っている（評価する取組みにおいて全ての項目を採用）
A.住宅以外の建築Rtlにおける設備騒音対策の評価する取組み
2,000㎡未満の基準で評価する。
|  |  |  | .Entire Building and Common Areas | 20: Dwelling and Accommodation Areas
|  |  |  | 0 | 20: 0; 25: ← 直接入力; 30: ON
1 | 1 |  |  | 1 | 1 | 設備騒音の種類 |  | 対策例 |  | 延床面積 | 7000 | Dwelling and Accommodation Areas | 0
2 | 2 |  |  |  | 25: 吹出し口、吸込み口からの騒音; 35: 低騒音型吹出し口、低騒音型吸込み口、位置、風量・風速の適正化など
3 | 3 |  |  | ○ | 20: ○; 25: 室内空調機からの騒音; 35: 防音カバー、位置など
4 | 4 |  |  |  | 20: ○; 25: 機械室からの騒音（透過騒音）; 35: 防音カバー、機械室の吸音・遮音、位置など; 45: 2,000㎡未満の建築Rtl
5 | 5 |  |  | ○ | 25: 同上（固体伝搬音）; 35: 防振架台、防振支持など; 45: 設備騒音の種類; 55: 対策例
0 | 0 |  |  | ○ | 25: ダクト・配管からの騒音（透過騒音）; 35: 消音ダクト、消音エルボ、消音ボックス、防音管巻き、位置など; 45: 配管からの騒音（透過騒音）; 55: 防音管巻き、位置など
|  |  |  | ○ | 25: 同上（固体伝搬音）; 35: 防振吊り、防振支持、フレキシブルジョイント、貫通部の防振施Fctなど; 45: 同上（固体伝播音）; 55: 防振吊り、防振支持、フレキシブルジョイント、貫通部の防振施Fctなど
[5 empty] | ○ | （屋外）冷却塔、室外機等からの騒音 |  | 防音塀、遮蔽体、防振支持、位置など |  | ビルマルチエアコン室内機等からの騒音 |  | 低騒音タイプの機器の採用など
|  |  |  | ○ | 20: ○; 25: （屋外）吸込み口・排気口からの騒音; 35: 位置、風量・風速の適正化など; 45: ビルマルチエアコン室外機等からの騒音; 55: 防音塀、遮蔽体、防振支持、位置など
|  |  |  | 0 | 20: 0; 25: 項目
B．住宅における設備騒音対策の評価する取組み
[5 empty] | 0 | ← 直接入力 | ON
1 | 1 |  |  |  | 20: 1; 25: 住宅; 35: Dwelling and Accommodation Areas; 40: 0
2 | 2 |  |  |  | 25: 設備騒音の種類; 35: 対策例
3 | 3 |  |  |  | 20: ○; 25: トイレ、浴室等の給配水音、排水音、使用音; 35: 適正な水圧、防音管巻き、管の防振支持金具、便器の防振支持、浴室の防振支持、位置など
4 | 4 |  |  |  | 20: ○; 25: ウォーターハンマー; 35: 適正な水圧、ウォーターハンマー防止器の採用など
5 | 5 |  |  |  | 25: エアコン室内機等からの騒音; 35: 低騒音タイプの機器の採用など
0 | 0 |  |  |  | 25: エアコン室外機からの騒音; 35: 防振ゴム、防振マット、低騒音タイプの機器
[5 empty] | ○ | 換気扇からの騒音 |  | 低騒音タイプの機器の採用など
[5 empty] | 0 | 項目
|  | 1.2 | Sound Insulation
1.2.1 Sound Insulation of Openings
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 0.6; 40: Dwelling and Accommodation Areas; 55: Weighting coef.(default) =; 60: 0
|  |  |  | 3 | 20: Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt; 40: 0; 45: Hsp,Htl,Apt
1 | 1 | bar: 20 to 35; 45
- | - |  |  | Level 1 | 20: 騒音が気になる。; 40: Level 1; 45: 騒音が気になる。
3 | 3 |  |  | Level 2 | 40: Level 2
- | - |  |  | Level 3 | 20: 騒音がほとんど気にならない。; 40: Level 3; 45: 騒音がほとんど気にならない。
5 | 5 |  |  | Level 4 | 40: Level 4
0 | 0 |  |  | Level 5 | 20: 騒音が気にならない; 40: Level 5; 45: 騒音が気にならない。
[5 empty] | 実施・竣工 |  |  |  |  | 実施・竣工
|  |  |  | Level 1 | 20: Less than T-1; 40: Level 1; 45: Lower than T-1
|  |  |  | Level 2 | 20: (No corresponding level); 40: Level 2; 45: (No corresponding level)
|  |  |  | ■Level 3 | 20: T-1; 40: Level 3; 45: T-1
|  |  |  | Level 4 | 20: (No corresponding level); 40: Level 4; 45: (No corresponding level)
|  |  |  | Level 5 | 20: T-2 or higher; 40: Level 5; 45: T-2 or higher
Outline of env. efforts | bar: 20
1.2.2 Sound Insulation of Partition Walls
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 0.4; 40: Dwelling and Accommodation Areas; 55: Weighting coef.(default) =; 60: 0
|  |  |  | 3 | 20: Off,Sch,Rst,Fct; 30: Hsp (Doctor’s Off.); 40: 3; 45: Hsp,Htl,Apt
1 | 1 | bar: 20 to 35; 45
2 | 2 |  |  | Level 1 | 20: 人の話し声が気になる。; 30: Hal話等の話の内容がわかる。; 40: Level 1; 45: テレビ、ラジオ、Hal話等の一般の発生音がかなり聞こえる。; 55: 隣戸の生活がかなり分かる。
3 | 3 |  |  | Level 2 | 40: Level 2
4 | 4 |  |  | Level 3 | 20: 人の話し声が気にならない。; 30: Hal話等の一般の発生音が小さく聞える。; 40: Level 3; 45: テレビ、ラジオ、Hal話等の一般の発生音が小さく聞こえる。; 55: 隣戸住宅の生活がわかるがあまり気にならない。
5 | 5 |  |  | Level 4 | 40: Level 4
0 | 0 |  |  | Level 5 | 20: 人の話し声がほとんど聞こえない。; 30: Hal話等の一般の発生音がほとんど聞えない。; 40: Level 5; 45: テレビ、ラジオ、Hal話等の一般の発生音が通常では聞こえない。; 55: 隣戸の気配を感じない。
[5 empty] | 実施・竣工 |  |  |  |  | 実施・竣工
|  |  |  | Level 1 | 20: Less than Dr-30; 30: Less than Dr-35; 40: Level 1; 45: Less than Dr-40
|  |  |  | Level 2 | 20: Dr-30; 30: Dr-35; 40: Level 2; 45: Dr-40
|  |  |  | ■Level 3 | 20: Dr-35; 30: Dr-40; 40: ■Level 3; 45: Dr-45
|  |  |  | Level 4 | 20: Dr-40; 30: Dr-45; 40: Level 4; 45: Dr-50
|  |  |  | Level 5 | 20: Dr-45 or higher; 30: Dr-50 or higher; 40: Level 5; 45: Dr-55 or higher
Outline of env. efforts | bar: 20
|  |  |  | 1.2.3 Sound Insulation Performance of Floor Slabs (light-weight impact source) | 60: <N.A.>
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 0; 40: Dwelling and Accommodation Areas; 55: Weighting coef.(default) =; 60: 0
|  |  |  | 3 | 20: Sch; 40: 3; 45: Hsp,Htl,Apt
1 | 1 | bar: 20 to 35; 45
2 | 2 |  |  | Level 1 | 20: 椅子の移動音、Rtlの落下音がかなりうるさい。; 40: Level 1; 45: 椅子の移動音、Rtlの落下音がかなり気になる。
3 | 3 |  |  | Level 2 | 40: Level 2
4 | 4 |  |  | Level 3 | 20: 椅子の移動音、Rtlの落下音がかなり気になる。; 40: Level 3; 45: 椅子の移動音、Rtlの落下音が小さく聞こえる。
5 | 5 |  |  | Level 4 | 40: Level 4
0 | 0 |  |  | Level 5 | 20: 椅子の移動音、Rtlの落下音が小さく聞こえる。; 40: Level 5; 45: 椅子の移動音、Rtlの落下音がほとんど聞こえない。
[5 empty] | 実施・竣工 |  |  |  |  | 実施・竣工
|  |  |  | Level 1 | 20: Worse than Lr-65; 40: Level 1; 45: Worse than Lr-55
|  |  |  | Level 2 | 20: Lr-65; 40: Level 2; 45: Lr-55
|  |  |  | ■Level 3 | 20: Lr-60; 40: ■Level 3; 45: Lr-50
|  |  |  | Level 4 | 20: Lr-55; 40: Level 4; 45: Lr-45
|  |  |  | Level 5 | 20: Lr-50 or better; 40: Level 5; 45: Lr-40 or better
Outline of env. efforts | bar: 20
|  |  |  | 1.2.4 Sound Insulation Performance of Floor Slabs (heavy-weight impact source) | 60: <N.A.>
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 0; 40: Dwelling and Accommodation Areas; 55: Weighting coef.(default) =; 60: 0
|  |  |  | 3 | 20: Sch; 40: 3; 45: Hsp,Htl,Apt
1 | 1 | bar: 20 to 35; 45
2 | 2 |  |  | Level 1 | 20: 人のとびはねや走り回る音がうるさい。; 40: Level 1; 45: 人のとびはねや走り回る音がかなり気になる。
3 | 3 |  |  | Level 2 | 40: Level 2
4 | 4 |  |  | Level 3 | 20: 人のとびはねや走り回る音がよく聞こえる。; 40: Level 3; 45: 人のとびはねや走り回る音が聞こえる。
5 | 5 |  |  | Level 4 | 40: Level 4
0 | 0 |  |  | Level 5 | 20: 人のとびはねや走り回る音が小さく聞こえる。; 40: Level 5; 45: 人のとびはねや走り回る音が聞こえるが意識することはあまりない。
[5 empty] | 実施・竣工 |  |  |  |  | 実施・竣工
|  |  |  | Level 1 | 20: Worse than Lr-65; 40: Level 1; 45: Worse than Lr-60
|  |  |  | Level 2 | 20: Lr-65; 40: Level 2; 45: Lr-60
|  |  |  | ■Level 3 | 20: Lr-60; 40: ■Level 3; 45: Lr-55
|  |  |  | Level 4 | 20: Lr-55; 40: Level 4; 45: Lr-50
|  |  |  | Level 5 | 20: Lr-50 or better; 40: Level 5; 45: Lr-45 or better
Outline of env. efforts | bar: 20
|  | 1.3 | Sound Absorption
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 0.2; 40: Dwelling and Accommodation Areas; 55: Weighting coef.(default) =; 60: 0
|  |  |  | 3 | 20: Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct; 40: 3; 45: Hsp,Htl
1 | 1 |  |  | Level 1 | 20: Sound absorbing materials are not used; 40: Level 1; 45: Sound absorbing materials are not used
- | - |  |  | Level 2 | 20: (No corresponding level); 40: Level 2; 45: (No corresponding level)
3 | 3 |  |  | ■Level 3 | 20: Sound absorbing materials are used in one of the following areas (walls, floor or ceiling); 40: ■Level 3; 45: Sound absorbing materials are used in one of the following areas (walls, floor or ceiling)
4 | 4 |  |  | Level 4 | 20: Sound absorbing materials are used in two of the following areas (walls, floor or ceiling); 40: Level 4; 45: Sound absorbing materials are used in two of the following areas (walls, floor or ceiling)
5 | 5 |  |  | Level 5 | 20: Sound absorbing materials are used in all of the following areas (walls, floor or ceiling); 40: Level 5; 45: Sound absorbing materials are used in all of the following areas (walls, floor or ceiling)
0 | 0 |  |  | Outline of env. efforts | bar: 20
|  | 2 | Thermal Comfort
|  | 2.1 | Room Temperature Control
2.1.1 Room Temperature
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 0.375; 50: Dwelling and Accommodation Areas; 60: 0
|  |  |  | 3 | Off,Hal (O.D.),Hal (Lib.) | Fct,Hsp (Waiting Room), Htl,Apt | Hsp (Doctor’s Off.) | Sch (Univ., etc.) | Sch (E.S./J.H.S./ H.S) | Rtl,Rst,Hal (oth.) | 3 | Hsp,Htl | Apt
1 | 1 | bar: 20 to 45; 55 to 60
2 | 2 |  |  | Level 1 | レベル２を満たさない。 | 冬期20℃、夏期28℃と多少我慢を強いる室温設定。 | 冬期21℃、夏期28℃と程度と多少我慢を強いる室温設定。 | 冬期10℃以上、夏期30℃以下と多少我慢を強いる室温設定。 | (該当するレベルなし) | 冬期18℃、夏期28℃程度と多少我慢を強いる室温設定。 | Level 1 | 冬期20℃、夏期28℃と多少我慢を強いる室温設定。 | 各室において冬期18℃、夏期28℃程度を強いる設定としている。
3 | 3 |  |  | Level 2 | 20: 冬期20℃、夏期28℃と多少我慢を強いる室温設定。; 40: (該当するレベルなし); 50: Level 2
4 | 4 |  |  | Level 3 | 一般的な冬期22℃、夏期26℃の設定。 | 一般的な冬期22℃、夏期26℃の設定。 | 一般的な冬期23℃、夏期26℃の設定。 | 一般的な冬期18～20℃、夏期25～28℃の設定。 | 冬期18℃以上、夏期28℃以下の範囲を設定している。 | 一般的な冬期20℃、夏期26℃の設定。 | Level 3 | 一般的な冬期22℃、夏期26℃の設定。 | 各居室において一般的な冬期22℃、夏期26℃を設定している。
5 | 5 |  |  | Level 4 | 40: 冬期20℃以上 、夏期25℃以下の設定。; 50: Level 4
0 | 0 |  |  | Level 5 | ASHRAE快適域やPOEM-Oを参考に冬期22℃～24℃、夏期24℃～26℃の範囲を設定している。 |  |  |  | 冬期22℃以上、夏期24℃以下の設定。 | ASHRAE快適域やPOEM-Oを参考に冬期20℃～22℃、夏期24℃～26℃の範囲を設定している。 | Level 5 | ASHRAE快適域やPOEM-Oを参考に冬期22℃～24℃、夏期24℃～26℃の範囲を設定している。 | 各居室において冬期22～24℃、夏期24～26℃の範囲を設定している。
[5 empty] | 実施・竣工 | [6 empty] | 実施・竣工
|  |  |  | Level 1 | Not adequate for Level 2. | Minimum equipment capacity to achieve room temperatures of 20˚C in winter and 28˚C in summer with some occupant discomfort | Minimum equipment capacity to achieve room temperatures of 21˚C in winter and 28˚C in summer with some occupant discomfort | The minimum equipment capacity is provided to achieve temperatures of 10˚C or more in winter and 30˚C or less in summer, which require tolerance of some discomfort | (No corresponding level) | Minimum equipment capacity to achieve room temperatures of 18˚C in winter and 28˚C in summer with some occupant discomfort | Level 1 | Minimum equipment capacity to achieve room temperatures of 20˚C in winter and 28˚C in summer with some occupant discomfort | Minimum equipment capacity to achieve room temperatures of 18˚C in winter and 28˚C in summer with some occupant discomfort
|  |  |  | Level 2 | 20: Minimum equipment capacity to achieve temperatures of 20˚C in winter and 28˚C in summer with some occupant discomfort; 40: (No corresponding level); 50: Level 2
|  |  |  | ■Level 3 | Sufficient equipment capacity to achieve general room temperatures of 22˚C in winter and 26˚C in summer | Sufficient equipment capacity to achieve general room temperatures of 22˚C in winter and 26˚C in summer | Sufficient equipment capacity to achieve general room temperatures of 23˚C in winter and 26˚C in summer | Sufficient equipment capacity for achieving commonly-applied room temperatures of 20˚C in winter and 27˚C in summer | Minimum equipment capacity to achieve room temperatures of 18˚C or higher in winter and 28˚C or lower in summer | Sufficient equipment capacity to achieve general room temperatures of 20˚C in winter and 26˚C in summer | ■Level 3 | Sufficient equipment capacity to achieve general room temperatures of 22˚C in winter and 26˚C in summer
|  |  |  | Level 4 | 40: Sufficient equipment capacity to achieve room temperatures of 20˚C or higher in winter and 25˚C or lower in summer; 50: Level 4
|  |  |  | Level 5 | 20: Sufficient equipment capacity to achieve room temperatures of 24˚C in both winter and summer; 40: Sufficient equipment capacity to achieving room temperatures of 22˚C or higher in winter and 24˚C or lower in summer; 45: Sufficient equipment capacity to achieve room temperatures of 22˚C in winter and 24˚C in summer; 50: Level 5; 55: Sufficient equipment capacity to achieve room temperature of 24˚C in both winter and in summer
|  |  |  | 2.1.2 負荷変動・追従制御性 | 35: <N.A.>
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 0
|  |  |  | 0 | 20: Sch・Rtl・Rst・Hal
1 | 1 |  |  | Level 1 | 20: 急激な負荷変動に対する考慮は特にしていない。
2 | 2 |  |  | Level 2
3 | 3 |  |  | Level 3 | 20: 一般的な負荷変動を考慮し、ある程度制御可能なシステムになっている。
4 | 4 |  |  | Level 4
5 | 5 |  |  | Level 5 | 20: 高度な負荷変動追従ができるような制御システムである。
0 | 0 |  |  | Outline of env. efforts | bar: 20
2.1.2 Perimeter Performance
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 0.25; 40: Dwelling and Accommodation Areas; 55: Weighting coef.(default) =; 60: 0
|  |  |  | 3 | 20: Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt; 40: 3; 45: Hsp,Htl; 55: Apt
1 | 1 | bar: 20 to 35; 45
2 | 2 |  |  | Level 1 | 20: 窓,外壁,屋根や床（特にピロティ）において室内への熱の侵入に対しての配慮が十分でなく、日射遮蔽性能や断熱性能が低い。; 40: Level 1; 45: 窓,外壁,屋根や床（特にピロティ）において室内への熱の侵入に対しての配慮が十分でなく、日射遮蔽性能や断熱性能が低い。; 55: 日本住宅性能表示基準「5-1断熱等性能等級」における等級1相当の屋根・外壁・床の部材構成、開口部の仕様を設定している。
3 | 3 |  |  | Level 2 | 40: Level 2; 55: 日本住宅性能表示基準「5-1断熱等性能等級」における等級2相当の屋根・外壁・床の部材構成、開口部の仕様を設定している。
4 | 4 |  |  | Level 3 | 20: 窓,外壁,屋根や床（特にピロティ）において、室内への熱の侵入に対しての配慮がなされており、実用上、日射遮蔽性能および断熱性能に問題がない。; 40: Level 3; 45: 窓,外壁,屋根や床（特にピロティ）において、室内への熱の侵入に対しての配慮がなされており、実用上、日射遮蔽性能および断熱性能に問題がない。; 55: 日本住宅性能表示基準「5-1断熱等性能等級」における等級3相当の屋根・外壁・床の部材構成、開口部の仕様を設定している。
5 | 5 |  |  | Level 4 | 40: Level 4; 55: (該当するレベルなし)
0 | 0 |  |  | Level 5 | 20: 窓,外壁,屋根や床（特にピロティ）において、室内への熱の侵入に対して、十分な配慮がなされており、最良の日射遮蔽性能および断熱性能を有する。; 40: Level 5; 45: 窓,外壁,屋根や床（特にピロティ）において、室内への熱の侵入に対して、十分な配慮がなされており、最良の日射遮蔽性能および断熱性能を有する。; 55: 日本住宅性能表示基準「5-1断熱等性能等級」における等級4相当の屋根・外壁・床の部材構成、開口部の仕様を設定している。
[5 empty] | 実施・竣工 |  |  |  |  | 実施・竣工
|  |  |  | Level 1 | 20: No attention has been paid to the infiltration of heat through window systems, outside walls, roof and floor (particularly where piloti are used), and insulation performance is poor. (Window system SC: around 0.7, U = 6.0 [W/m2K], outer walls and others: U = 3.0 [W/m2K]); 40: Level 1; 45: No attention has been paid to the infiltration of heat through window systems, outside walls, roof and floor (particularly where piloti are used), and insulation performance is poor. (Window system SC: around 0.7, U = 6.0 [W/m2K], outer walls and others: U = 3.0 [W/m2K]); 55: Not adequate for Level 2.
|  |  |  | Level 2 | 40: Level 2; 55: Requirements for Grade 3 in 5-1 Thermal Insulation Performance Grade of the Japan Housing Performance Indication Standard are satisfied.
|  |  |  | ■Level 3 | 20: Attention has been paid to the infiltration of heat to the interior through windows, outside walls, roof and floor (particularly where piloti are used), and there is no practical problem with insolation blocking and insulation performance. (Window system SC: around 0.5, U = 4.0 [W/m2K], outer walls and others: U = 2.0 [W/m2K]); 40: ■Level 3; 45: Attention has been paid to the infiltration of heat to the interior through windows, outside walls, roof and floor (particularly where piloti are used), and there is no practical problem with insolation blocking and insulation performance. (Window system SC: around 0.5, U = 4.0 [(W/m2K], outer walls and others: U = 2.0 [W/m2K]); 55: Requirements for Grade 4 in 5-1 Thermal Insulation Performance Grade of the Japan Housing Performance Indication Standard are satisfied.
|  |  |  | Level 4 | 40: Level 4; 55: Requirements for Grade 5 in 5-1 Thermal Insulation Performance Grade of the Japan Housing Performance Indication Standard are satisfied.
|  |  |  | Level 5 | 20: Close attention has been paid to the infiltration of heat to the interior through windows systems, outside walls, roof and floor (particularly where piloti are used), and the building has the highest level of insolation blocking and insulation performance. (Window system SC: around 0.2, U = 3.0 [W/m2K], outer walls and others: U = 1.0 [W/m2K]); 40: Level 5; 45: Close attention has been paid to the infiltration of heat to the interior through windows systems, outside walls, roof and floor (particularly where piloti are used), and the building has the highest level of insolation blocking and insulation performance. (Window system SC: around 0.2, U = 3.0 [W/m2K], outer walls and others: U = 1.0 [W/m2K]); 55: Requirements for Grade 6 or above in 5-1 Thermal Insulation Performance Grade of the Japan Housing Performance Indication Standard are satisfied.
|  |  |  | Outline of env. efforts | 20: sample input; Introduction of airflow windows
|  |  |  | Window system SC | 30: window solar heat gain coef(η)
|  |  |  | U value [W/m2K] | 20: window system; 30: roof; 40: outer walls; 50: floor
|  |  |  | Dwelling area: | 20: Window system U value; 30: perimeter UA value; 40: ηAC; 50: ηAH
2.1.3 Zoned Control
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 0.375; 50: examples of HVAC systems; 60: Remarks
|  |  |  | 3 | 20: Off,Hal(Lib.)(O.D.),Hsp,Htl,Fct; 35: Rtl,Rst,Hal(oth.)
1 | 1 |  |  | Level 1 | 20: No distinction is made between orientation directions, or between perimeter and interior, and only one air conditioning system is planned*1, which must be switched between heating and cooling for each season; 35: There is no zoning of heating and cooling within a single floor, and a single-circuit air conditioning system is planned. Switching between heating and cooling is required for the selection of air conditioning modes.; 50: Single duct system, two-pipe FCU system (no zoning, switching between heating and cooling).; 60: For Hal (oth.), museums and exhibition facilities will not be applicable.
2 | 2 |  |  | Level 2
3 | 3 |  |  | ■Level 3 | 20: There are air conditioning zoning*1 that differentiates between orientation directions, between perimeter and interior, and between internal load distributions. The air conditioning system can provide either heating or cooling separately to each zone.; 35: Each floor is divided into multiple zones according to their thermal loads, and the air conditioning system is planned to allow either heating or cooling in each zone.; 50: Single duct system, two-pipe FCU system (zoning grade assessment, switching between heating and cooling).
4 | 4 |  |  | Level 4 | 20: There is air conditioning zoning at around the standard of level 3*1, and the system also allows selection between cooling and heating for each zone.; 35: There is air conditioning zoning at around the standard of level 3, and the planned system also allows selection between cooling and heating for each zone.; 50: Double duct system (4 pipes for AHU), four-pipe FCU system, task/ambient air conditioning system (evaluate both the zoning grade and simultaneous heating and cooling).
5 | 5 |  |  | Level 5 | 20: There are separate air conditioning systems for each orientation direction, and for perimeter and interior*1, allowing more detailed zoning (broadly, zones of 40 m2 or less). The air conditioning system can provide either heating or cooling separately to each zone.; 35: Each floor is divided into many small zones for individual sales areas or tenants, and the air conditioning system is planned to allow either heating or cooling in zone units.; 50: Multi-unit heat pump system (simultaneous heating and cooling), double duct system (4 pipes for AHU), and four-pipe FCU system level with more detailed zoning than levels 3 and 4 (zones of around 40 m2).
0 | 0
|  |  |  | 2.1.5 温度・湿度制御 | 35: <N.A.>
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 0; 40: Dwelling and Accommodation Areas; 55: Weighting coef.(default) =; 60: 0
|  |  |  | 0 | 20: Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt; 40: 0; 45: Hsp・Htl
1 | 1 |  |  | Level 1 | 20: ＯＮ-ＯＦＦによる温度・湿度制御になっている。; 40: Level 1; 45: ＯＮ-ＯＦＦによる温度・湿度制御になっている。
2 | 2 |  |  | Level 2 | 20: 比例制御、多位置制御による温度・湿度制御になっている。; 40: Level 2; 45: 比例制御、多位置制御による温度・湿度制御になっている。
3 | 3 |  |  | Level 3 | 20: ＰＩＤ制御による温度・室内湿度になっている。; 40: Level 3; 45: ＰＩＤ制御による温度・室内湿度になっている。
4 | 4 |  |  | Level 4 | 40: Level 4
5 | 5 |  |  | Level 5 | 20: 快適センサーなどによる温度・湿度制御（快適範囲における温度制御）が可能である。; 40: Level 5; 45: 快適センサーなどによる温度・湿度制御（快適範囲における温度制御）が可能である。
0 | 0
|  |  |  | 2.1.6 個別制御 | 35: <N.A.>
|  |  |  | Dwelling and Accommodation Areas | 30: Weighting coef.(default) =; 35: 0
|  |  |  | 0 | 20: Hsp・Htl; 30: Apt
1 | 1 |  |  | Level 1 | 20: 在室者は手元で、Low-Middle-Highの風量切り替えが可能である。; 30: レベル３を満たさない。
2 | 2 |  |  | Level 2
3 | 3 |  |  | Level 3 | 20: 在室者は手元で、直接温度設定やLow-Middle-Highの風量調整が可能である。ただし、熱源側は季節に応じて冷暖切り替えである。; 30: 各室内で温度設定が可能。
4 | 4 |  |  | Level 4
5 | 5 |  |  | Level 5 | 20: 在室者は手元で、直接、温度設定や風量調整が可能である。（熱源側は冷暖同時）; 30: 住戸内の温度を設定しつつ、各室において温度の個別設定が可能。
0 | 0
|  |  |  | 2.1.7 時間外空調に対する配慮 | 35: <N.A.>; 40: 2.1.8 監視システム; 60: <N.A.>
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 0; 40: Entire Building and Common Areas; 55: Weighting coef.(default) =; 60: 0
|  |  |  | 0 | 20: Off・Sch・Hsp・Htl・Fct; 40: 0; 45: Rtl・Rst
1 | 1 |  |  | Level 1 | 20: 時間外や休日時には、空調運転を行わない。; 40: Level 1; 45: 同一フロアで熱負荷別に複数にゾーニングがなされておらず、代表的なゾーン監視のためにセンサー等の監視システムが設置されている。
2 | 2 |  |  | Level 2 | 40: Level 2
3 | 3 |  |  | Level 3 | 20: 時間外や休日時には、居住者のフロア全体が空調可能なシステムとなっている。; 40: Level 3; 45: 同一フロアで熱負荷別に複数にゾーニングがなされており、複数ゾーン監視のために制御センサとは別に複数の監視・計測用センサがある監視システムが設置されている。
4 | 4 |  |  | Level 4 | 40: Level 4
5 | 5 |  |  | Level 5 | 20: 時間外や休日時には、居住者のゾーンのみ空調可能なシステムとなっている。; 40: Level 5; 45: 同一フロアで、売り場・テナント用に細かくゾーニングがなされており、それを細かく監視するために制御センサとは別に複数の監視・計測用センサがある監視システムが設置されている。
0 | 0 |  |  | Outline of env. efforts | bar: 20
|  | 2.2 | Humidity Control |  | 35: <N.A.>
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 0.2; 40: Dwelling and Accommodation Areas; 55: Weighting coef.(default) =; 60: 0
|  |  |  | 0 | Off,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  | Sch(Univ. etc.) | Sch(E.S./J.H.S./H.S.) | 3 | Hsp,Htl |  | Apt
1 | 1 | bar: 20 to 35; 45
2 | 2 |  |  | Level 1 | レベル３を満たさない。 |  | レベル３を満たさない。 | レベル３を満たさない。 | Level 1 | レベル３を満たさない。 |  | 何も配慮していない。
3 | 3 |  |  | Level 2 | 40: Level 2; 55: (該当するレベルなし)
4 | 4 |  |  | Level 3 | 加湿機能を有し、かつ一般的な冬期40％、夏期50％の設定で計画されている。 |  | 加湿機能を有し、かつ一般的な冬期40～70％、夏期50～65％。の範囲で計画されている。 | 一般的な冬期30～45％、夏期55％～80％の範囲で計画されている。 | Level 3 | 加湿機能を有し、かつ一般的な冬期40％、夏期50％の設定で計画されている。 |  | 適切な換気機能を有し、熱橋となる部分の断熱補強、防湿層、通気層の設置等の結露防止対策がとられている。
5 | 5 |  |  | Level 4 | 40: Level 4; 55: 除湿機能を有し、熱橋となる部分の断熱補強、防湿層、通気層の設置等の結露防止対策がとられている。
0 | 0 |  |  | Level 5 | 加湿・除湿機能を有し、かつASHRAE快適域やPOEM-Oを参考に45％～55％の範囲で計画されている。 |  | 加湿・除湿機能を有し、ASHRAE快適域やPOEM-Oを参考に45％～55％の範囲で計画されている。 | 加湿・除湿機能を有し、ASHRAE快適域やPOEM-Oを参考に45％～55％の範囲で計画されている。 | Level 5 | 加湿・除湿機能を有し、かつASHRAE快適域やPOEM-Oを参考に45％～55％の範囲で計画されている。 |  | 加湿・除湿機能を有し、45％～55％の快適範囲を設定し、なおかつ、熱橋となる部分の断熱補強、防湿層、通気層の設置等の結露防止対策がとられている。
[5 empty] | 実施・竣工 |  |  |  |  | 実施・竣工
|  |  |  | Level 1 | Not adequate for level 3. |  | Not adequate for level 3. | Not adequate for level 3. | Level 1 | Not adequate for level 3. |  | No consideration given.
|  |  |  | Level 2 | 40: Level 2; 55: (No corresponding level)
|  |  |  | Level 3 | Humidification equipment is available, and equipment capacity is generally sufficient to keep humidity to 50% in summer and 40% in winter. |  | Humidification equipment is also available, and equipment capacity is generally sufficient to keep humidity to 40-70% in winter and 50-65% in summer. | Sufficient equipment capacity to achieve general indoor humidity of 30 to 45% in winter and 55 to 80% in summer. | ■Level 3 | Sufficient equipment capacity with humidifier to achieve general humidity of 50% in summer and 40% in winter. |  | Appropriate ventilation functions are provided, and anti-condensation measures have been taken on elements that can act as heat bridges, such as insulation reinforcement, humidity barriers and permeable layers.
|  |  |  | Level 4 | 40: Level 4; 55: Dehumidification functions are provided, and anti-condensation measures have been taken on elements that can act as heat bridges, such as insulation reinforcement, humidity barriers and permeable layers.
|  |  |  | Level 5 | Humidification and dehumidification equipment is available, and equipment capacity is sufficient to keep humidity in the range 45-55%. |  | Humidification and dehumidification equipment is available, and equipment capacity is sufficient to keep humidity in the range 45-55%. | Sufficient equipment capacity with humidifier/dehumidifier to achieve humidity of 45 to 55%. | Level 5 | Humidification and dehumidification equipment is available, and equipment capacity is sufficient to keep humidity in the range 45-55%. |  | Dehumidification and humidification functions are provided and set to a comfort range of 45-55%, and anti-condensation measures have been taken on elements that can act as heat bridges, such as insulation reinforcement, humidity barriers and permeable layers.
Outline of env. efforts | bar: 20
|  | 2.3 | Type of Air Conditioning System
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 0.3; 40: Dwelling and Accommodation Areas; 55: Weighting coef.(default) =; 60: 0
|  |  |  | 3 | 20: Off,Sch,Rtl,Rst,Hal,Hsp(Waiting Room),Htl,Fct,Apt; 30: Hsp(Doctor's Off); 40: 3; 45: Hsp,Htl; 55: Apt
1 | 1 | bar: 20 to 35; 45
2 | 2 |  |  | Level 1 | 20: The air conditioning system was planned with no particular consideration for the vertical temperature distribution and airflow speed in occupancy zone.; 30: Air conditioning system designed without specific consideration of vertical temperature variation and air flow in occupied areas; 40: Level 1; 45: The air conditioning system was planned with no particular consideration for the vertical temperature distribution and airflow speed in occupancy zone.; 55: Air conditioning system designed without specific consideration of vertical temperature variation and air flow in air-conditioned occupied areas, or of temperature difference between air-conditioned and non-air-conditioned areas
3 | 3 |  |  | Level 2 | 40: Level 2
4 | 4 |  |  | Level 3 | 20: The air conditioning system is normal, but the air supply and extraction plan considered the vertical temperature distribution and airflow speed in occupancy zone.; 30: The air conditioning system is normal, but the air supply and extraction plan considered the vertical temperature distribution and airflow speed in occupancy zone, and the partitions in the medical examining rooms.; 40: Level 3; 45: The air conditioning system is normal, but the air supply and extraction plan considered the vertical temperature distribution and airflow speed in occupancy zone.; 55: Air conditioning system designed in consideration of vertical temperature variation and air flow in air-conditioned occupied areas, or of temperature difference between air- conditioned and non-air-conditioned areas
5 | 5 |  |  | Level 4 | 40: Level 4
0 | 0 |  |  | Level 5 | 20: The air conditioning system was chosen to mitigate the vertical temperature distribution and airflow speed in the room.; 30: The air conditioning system was chosen to mitigate the vertical temperature distribution and airflow speed in occupancy zone, and to consider the partitions of the doctor's offices.; 40: Level 5; 45: The air conditioning system was chosen to mitigate the vertical temperature distribution and airflow speed in occupancy zone.; 55: and non-air-conditioned areas
[5 empty] | 実施・竣工 |  |  |  |  | 実施・竣工
|  |  |  | Level 1 | 20: 居住域の上下温度差や気流速度について特に配慮していない空調方式が計画されている。; 30: 居住域の上下温度差や気流速度について特に配慮していない空調方式が計画されている。; 40: Level 1; 45: 居住域の上下温度差や気流速度について特に配慮していない空調方式が計画されている。; 55: 空調居住域の上下温度差、気流速度や非空調部屋との室間温度差などについて特に配慮していない空調方式が採用されている。
|  |  |  | Level 2 | 40: Level 2
|  |  |  | ■Level 3 | 20: 通常の空調方式であるが、居住域の上下温度差や気流速度に配慮した給排気計画がされている。上下温度差及び気流速度の目標値をおおよそ5℃以内、0.35m/s程度に設定している。; 30: 通常の空調方式であるが、居住域の上下温度差や気流速度および診療室内の間仕切りなどに配慮した給排気計画がされている。上下温度差及び気流速度の目標値をおおよそ5℃以内、0.35m/s程度に設定している。; 40: ■Level 3; 45: 通常の空調方式であるが、居住域の上下温度差や気流速度に配慮した給排気計画がされている。上下温度差及び気流速度の目標値をおおよそ5℃以内、0.35m/s程度に設定している。; 55: 空調居住域の上下温度差、気流速度の目標値をおおよそ4℃以内、0.4m/s程度に設定している。トイレ・浴室などを含めた非空調部分でもスポット的空調対応が可能で、室間温度差を軽減することができる。
|  |  |  | Level 4 | 40: Level 4
|  |  |  | Level 5 | 20: 居住域の上下温度差や気流速度が少なくなるように配慮された空調方式＊が採用されている。あるいは、その他の空調方式で、上下温度差および気流速度の目標値をおおよそ2℃以内、0.15m/s程度に設定している。; 30: 居住域の上下温度差や気流速度が少なくなり、また診療室内の間仕切りに配慮された空調方式＊が採用されている。あるいは、その他の空調方式で、上下温度差および気流速度の目標値をおおよそ2℃以内、0.15m/s程度に設定している。; 40: Level 5; 45: 居住域の上下温度差や気流速度が少なくなるように配慮された空調方式＊が採用されている。上下温度差および気流速度の目標値をおおよそ2℃以内、0.15m/s程度に設定している。; 55: 空調居住域の上下温度差、気流速度の目標値をおおよそ2℃以内、0.2m/s程度に設定している。トイレ・浴室などを含めた全室が空調可能とし、室間温度差を無くすことができる。
＊ 例えば、天井・床輻射冷暖房方式や床吹出し方式などを指す。
|  |  |  | 2.3.1 上下温度差 | 35: <N.A.>; 40: 2.3.2 平均気流速度; 60: <N.A.>
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 0; 40: Entire Building and Common Areas; 55: Weighting coef.(default) =; 60: 0
|  |  |  | 0 | 20: Off・Sch・Rtl・Rst・Hal・Hsp（待・診）・Htl・Fct・住; 40: 0; 45: Off・Sch・Rtl・Rst・Hal・Hsp（待・診）・Htl・Fct・住
1 | 1 |  |  | Level 1 | 20: 5℃＜ [上下温度差]; 40: Level 1; 45: 0.45ｍ/ｓ＜ [平均気流速度]
2 | 2 |  |  | Level 2 | 40: Level 2; 45: 0.35ｍ/ｓ＜ [平均気流速度] ≦0.45ｍ/ｓ
3 | 3 |  |  | Level 3 | 20: 2℃＜ [上下温度差] ≦5℃; 40: Level 3; 45: 0.25ｍ/ｓ＜ [平均気流速度] ≦0.35ｍ/ｓ
4 | 4 |  |  | Level 4 | 40: Level 4; 45: 0.15ｍ/ｓ＜ [平均気流速度] ≦0.25ｍ/ｓ
5 | 5 |  |  | Level 5 | 20: [上下温度差] ≦2℃; 40: Level 5; 45: [平均気流速度] ≦0.15ｍ/ｓ
0 | 0 |  |  | Outline of env. efforts | bar: 20
|  | 3 | Lighting & Illumination
|  | 3.1 | Daylight
3.1.1 Daylight Factor
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 0.6; 40: Dwelling and Accommodation Areas; 55: Weighting coef.(default) =; 60: 0
|  |  |  | 3 | 20: Off,Sch,Hal(Lib.),Hsp,Htl,Fct,Apt; 40: 3; 45: Hsp,Htl; 55: Apt
1 | 1 |  |  | Level 1 | 20: [Daylight factor] < 1.0%; 40: Level 1; 45: [Daylight factor] < 0.5%; 55: [Daylight factor] < 0.5%
2 | 2 |  |  | Level 2 | 20: 1.0% ≦ [Daylight factor] < 1.5%; 40: Level 2; 45: 0.5% ≦ [Daylight factor] < 0.75%; 55: 0.5% ≦ [Daylight factor] < 1.0%
3 | 3 |  |  | ■Level 3 | 20: 1.5% ≦ [Daylight factor] < 2.0%; 40: ■Level 3; 45: 0.75% ≦ [Daylight factor] < 1.0%; 55: 1.0% ≦ [Daylight factor] < 1.5%
4 | 4 |  |  | Level 4 | 20: 2.0% ≦ [Daylight factor] < 2.5%; 40: Level 4; 45: 1.0% ≦ [Daylight factor] < 1.25%; 55: 1.5% ≦ [Daylight factor] < 2.0%
5 | 5 |  |  | Level 5 | 20: 2.5% ≦ [Daylight factor]; 40: Level 5; 45: 1.25% ≦ [Daylight factor]; 55: 2.0% ≦ [Daylight factor]
0 | 0 |  |  | Outline of env. efforts | bar: 20
Daylight factor | bar: 20
|  |  |  | 3.1.2 Openings by Orientation | 35: <N.A.>
|  |  |  | Dwelling and Accommodation Areas | 30: Weighting coef.(default) =; 35: 0
|  |  |  | 3 | 20: Apt
1 | 1 |  |  | Level 1 | 20: No south-facing windows
- | 2 |  |  | Level 2 | 20: (No corresponding level)
3 | 3 |  |  | ■Level 3 | 20: South-facing windows
- | 4 |  |  | Level 4 | 20: (No corresponding level)
5 | 5 |  |  | Level 5 | 20: South and east-facing windows
0 | 0 |  |  | Outline of env. efforts | bar: 20
3.1.3 Daylight Devices
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 0.4; 40: Dwelling and Accommodation Areas; 55: Weighting coef.(default) =; 60: 0
|  |  |  | 3 | 20: Off,Sch,Fct; 30: Rtl,Rst,Hal(Lib.),Hsp, Htl,Apt; 40: 3; 45: Hsp,Htl,Apt
- | - |  |  | Level 1 | 20: (No corresponding level); 30: (No corresponding level); 40: Level 1; 45: (No corresponding level)
- | - |  |  | Level 2 | 20: (No corresponding level); 30: (No corresponding level); 40: Level 2; 45: (No corresponding level)
3 | 3 |  |  | ■Level 3 | 20: There are no daylight devices.; 30: There are no daylight devices.; 40: ■Level 3; 45: There are no daylight devices.
4 | - |  |  | Level 4 | 20: There is one type of daylight device.; 30: (No corresponding level); 40: Level 4; 45: (No corresponding level)
5 | 5 |  |  | Level 5 | 20: There are two or more types of daylight device, or they have advanced functions.; 30: There are some daylight devices.; 40: Level 5; 45: There are some daylight devices.
0 | 0 |  |  | Outline of env. efforts | 40: Note; Describe introduced technics.
|  | 3.2 | Anti-glare Measures
|  |  |  | 3.2.1 照明器具のグレア | 35: <N.A.>
|  |  |  | 建Rtl全体,共用部分 | 30: Weighting coef.(default) =; 35: 0; 40: Dwelling and Accommodation Areas; 55: Weighting coef.(default) =; 60: 0
|  |  |  | 0 | 20: Off,Sch,Hsp,Htl,Fct,Apt; 40: 0; 45: Hsp,Htl,Apt
1 | 1 |  |  | 0 | 20: 水平方向から見て光源が露出し、グレアを制限していない器具。G3分類の器具。; 40: Level 1; 45: 水平方向から見て光源が露出しグレアを制限していない器具。G3分類の器具。
- | - |  |  | 0 | 20: (該当するレベルなし); 40: Level 2; 45: (該当するレベルなし)
3 | 3 |  |  | 0 | 20: 水平方向から見て光源が露出せず、グレアを制限している器具。G2分類の器具。; 40: Level 3; 45: 水平方向から見て光源が露出せずグレアを制限している器具。G2分類の器具。
- | - |  |  | 0 | 20: (該当するレベルなし); 40: Level 4; 45: (該当するレベルなし)
5 | 5 |  |  | 0 | 20: 反射板形状のFct夫、ルーバー・透光性カバーなどにより、十分にグレアを制限している器具。G1、G0、V分類の器具。; 40: Level 5; 45: 反射板形状のFct夫、ルーバー・透光性カバーなどにより十分にグレアを制限している器具。G1、G0、V分類の器具。
0 | 0
3.2.1 Daylight Control
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 1; 40: Dwelling and Accommodation Areas; 55: Weighting coef.(default) =; 60: 0
|  |  |  | 3 | 20: Off,Sch(Univ. etc.),Hsp,Htl,Fct,Apt; 30: Sch(E.S./J.H.S./H.S.); 40: 3; 45: Hsp,Htl,Apt
1 | 1 |  |  | Level 1 | 20: No countermeasures.; 30: No countermeasures.; 40: Level 1; 45: No countermeasures.
2 | - |  |  | Level 2 | 20: Glare is controlled with screens, awnings and eaves.; 30: (No corresponding level); 40: Level 2; 45: (No corresponding level)
3 | 3 |  |  | ■Level 3 | 20: Glare is controlled with blinds, or by a combination of any two among screens, awnings and eaves.; 30: Glare is controlled with screens, awnings and eaves.; 40: ■Level 3; 45: Glare is controlled with curtains, screens, awnings and eaves.
4 | 4 |  |  | Level 4 | 20: Glare is controlled with blinds, together with any of one among screens, awnings and eaves.; 30: Glare is controlled with blinds or any combination of two or more fixtures including curtains, screens, awnings and eaves; 40: Level 4; 45: Glare is controlled with blinds, or a combination of any two among curtains, screens, awnings and eaves.
5 | 5 |  |  | Level 5 | 20: Glare is controlled with automatically-controlled blinds.; 30: Glare is controlled with blinds and at least one other fixture, including curtains, screens, awnings and eaves; 40: Level 5; 45: Glare is controlled with blinds, together with any of one among curtains, screens, awnings and eaves.
0 | 0 |  |  | Outline of env. efforts | 40: Note; Describe introduced technics.
|  |  |  | 3.2.2 Reflection Control | 35: <N.A.>
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 0
既存 |  |  |  | 0 | 20: Sch(E.S./J.H.S./H.S.)
1 |  |  |  | Level 1 | 20: レベル３を満たさない。
- |  |  |  | Level 2 | 20: (該当するレベルなし)
3 |  |  |  | Level 3 | 20: 教室内で視界に見え方を妨害するような「まぶしさ」を感じさせる強い光源がないこと。 （解説（ア）～（ウ））
- |  |  |  | Level 4 | 20: (該当するレベルなし)
5 |  |  |  | Level 5 | 20: レベル３を満たし、かつ、カーテンを使用する、などの運用面の取り組みを行っている。
0 |  |  |  | Outline of env. efforts | 40: 30字以内で記入
判定表
[5 empty] | 評価項目 | 判定基準
[5 empty] | （ア） | 児童生徒等から見て、黒板の外側15°以内の範囲に輝きの強い光源（昼光の場合は窓）がない。
[5 empty] | （イ） | 見え方を妨害するような光沢が、黒板及び机上面にない。
[5 empty] | （ウ） | 見え方を妨害するような電灯や明るい窓等が、テレビ及びコンピュータ等の画面に映じていない。
|  | 3.3 | Illuminance Level
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 0.15; 50: Dwelling and Accommodation Areas; 60: 0
|  |  |  | 3 | Off,Hsp(Doctor's Off),Hal(Lib.),Fct |  | Sch | Hsp(Waiting Room) | Htl | Apt | 3 | Hsp | Htl,Apt
1 | 1 |  |  | Level 1 | (No corresponding level) |  | [Illuminance] < 300 lx | [Illuminance] < 150 lx | [Illuminance] < 100 lx | [Illuminance] < 100 lx | Level 1 | [Illuminance] < 150 lx | [Illuminance] < 100 lx
2 | - |  |  | Level 2 | [Illuminance] <300 lx, or 1,000 lx ≦ [Illuminance] |  | (No corresponding level) | (No corresponding level) | (No corresponding level) | (No corresponding level) | Level 2 | (No corresponding level) | (No corresponding level)
3 | 3 |  |  | ■Level 3 | Overall lighting system: |  | 300 lx ≦ [Illuminance] < 500 lx, or 750 lx ≦ [Illuminance] | 150 lx ≦ [Illuminance] | 100 lx ≦ [Illuminance] | 100 lx ≦ [Illuminance] | ■Level 3 | 150 lx ≦ [Illuminance] | 100 lx ≦ [Illuminance]
4 | 4 |  |  | Level 4 | 300 lx ≦ [Illuminance] < 500 lx; |  | 500 lx ≦ [Illuminance] < 750 lx | Equivalent to level 3 and 100 lx ≦ [vertical illuminance] for walls | (No corresponding level) | Equivalent to level 3 and 100 lx ≦ [vertical illuminance] for walls | Level 4 | Equivalent to level 3 and a [vertical illuminance] for walls of 100 lx or higher | (No corresponding level)
5 | 5 |  |  | Level 5 | In cases of the task/ambient lighting system or its equivalent, -the task illuminance is more than 500 lx and less than 1,000 lx, and -the ambient illuminance is more than 1/3 and less than 2/3 of the task illuminance, and -the illuminance of vertical surfaces of the walls is 100 lx or more and the reflectance is 30% or more, or horizontal surfaces of the ceiling is 100 lx or more and the reflectivity is 50% or more. |  | (No corresponding level) | (No corresponding level) | (No corresponding level) | (No corresponding level) | Level 5 | (No corresponding level) | Equivalent to level 3 and individual controls of multiple devices
0 | 0
|  |  |  | 3.3.2 照度均斉度 | 30: Weighting coef.(default) =; 35: 0; 55: Weighting coef.(default) =; 60: 0
|  |  |  | 3 | 20: Entire Building and Common Areas; 40: 3; 45: Dwelling and Accommodation Areas
[5 empty] | Off,Sch,Hsp(Doctor's Off),Htl,Fct,Apt |  |  |  |  | Hsp
|  |  |  | Level 1 | 20: 全般照明方式の場合で室内にかなり不快に感じる程度の非常に暗い部分がある。; 40: Level 1; 45: 全般照明方式の場合で室内にかなり不快に感じる程度の非常に暗い部分がある。
|  |  |  | Level 2 | 20: 全般照明方式の場合で室内にやや不快に感じる程度の暗い部分がある。; 40: Level 2; 45: 全般照明方式の場合で室内にやや不快に感じる程度の暗い部分がある。
|  |  |  | ■Level 3 | 20: 全般照明方式の場合で室内に許容できる程度の暗い部分がある。タスク・アンビエント照明方式の場合で作業面の明るさと周りの明るさのバランスが不十分。; 40: ■Level 3; 45: 全般照明方式の場合で室内に許容できる程度の暗い部分がある。タスク・アンビエント照明方式の場合で作業面の明るさと周りの明るさのバランスが不十分。
|  |  |  | Level 4 | 20: 全般照明方式の場合で室内にほとんど暗い部分がない。; 40: Level 4; 45: 全般照明方式の場合で室内にほとんど暗い部分がない。
|  |  |  | Level 5 | 20: 全般照明方式の場合で室内に暗い部分がない。タスク・アンビエント照明方式の場合で作業面の明るさと周りの明るさのバランスが良い。; 40: Level 5; 45: 全般照明方式の場合で室内に暗い部分がない。タスク・アンビエント照明方式の場合で作業面の明るさと周りの明るさのバランスが良い。
Outline of env. efforts | bar: 20
|  | 3.4 | Lighting Controllability
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 0.25; 40: Dwelling and Accommodation Areas; 55: Weighting coef.(default) =; 60: 0
|  |  |  | 3 | Off,Sch(Univ. etc.),Hal(oth.), Rtl,Hsp,Htl,Fct,Apt |  | Sch(E.S./J.H.S./H.S.) | Remarks | 3 | Hsp |  | Htl,Apt
1 | 1 |  |  |  | 20: 基本; 35: Hal（その他）において、博Rtl館・展示施設は評価対象外; 45: 基本
- | - |  |  | Level 1 | 20: 照明制御ができない。; 30: 明るさやSch習形態に応じた制御区画ではない。; 40: Level 1; 45: 照明制御ができない。; 55: 照明制御ができない。
3 | 3 |  |  | Level 2 | 20: (該当するレベルなし); 30: (該当するレベルなし); 40: Level 2; 45: (該当するレベルなし); 55: (該当するレベルなし)
- | - |  |  | Level 3 | 20: 執務者・売り場等について複数単位の大まかな照明制御ができる。; 30: 明るさやSch習形態に応じた制御区画であり、在室者自らが点灯・消灯によって制御できる; 40: Level 3; 45: 複数ベッド単位の大まかな照明制御ができる。; 55: 室内で大まかな照明制御ができる。
5 | 5 |  |  | Level 4 | 20: (該当するレベルなし); 30: (該当するレベルなし); 40: Level 4; 45: (該当するレベルなし); 55: (該当するレベルなし)
0 | 0 |  |  | Level 5 | 20: 各執務者・売り場等の部分について、細かな照明制御ができる、または、自動照明制御ができる。; 30: レベル３を満たしている。かつ、部分的に自動調光ができる。; 40: Level 5; 45: ベッド単位の細かな照明制御ができる。; 55: 室内の複数部分に対して細かい照明制御ができる、または、自動照明制御ができる。
[5 empty] | 実施・竣工 |  |  |  |  | 実施・竣工
|  |  |  | Level 1 | Lighting control is not zoned and no control panel/devices are available for adjustment |  | Lighting control is not zoned in accordance with illuminance levels and learning methods | For Hal (oth.), only museums and exhibition facilities are applicable, and only the exhibition rooms will be evaluated. | Level 1 | No lighting control is available |  | No lighting control is available
|  |  |  | Level 2 | 20: (No corresponding level); 40: Level 2; 45: (No corresponding level)
|  |  |  | ■Level 3 | 20: Lighting control per four-task unit is available or control panel/devices are available for adjustment; 30: Lighting control is zoned in accordance with illuminance levels and learning methods, and on/off control by the occupants is available; 40: ■Level 3; 45: Lighting control per multi-bed unit is available or control panel/devices for adjustment are available; 55: Control panel/devices are available for broad lighting adjustment for the entire room
|  |  |  | Level 4 | 20: (No corresponding level); 40: Level 4; 45: (No corresponding level)
|  |  |  | Level 5 | 20: Lighting control per task unit is available and adjustment via computer terminal/remote control or automatic control is available; 30: Level 3 is satisfied and automatic lighting adjustment is partially available; 40: Level 5; 45: Detailed lighting control per bed is available; 55: Detailed lighting control per multi-zone unit is available via computer terminal/remote control OR automatic control system
Outline of env. efforts | bar: 20
|  | 4 | Air Quality
|  | 4.1 | Source Control
4.1.1 Chemical Pollutants
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 1; 40: Dwelling and Accommodation Areas; 55: Weighting coef.(default) =; 60: 0
|  |  |  | 3 | 20: Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt; 30: Sch（ES/JS/JHS）; 40: 3; 45: Hsp,Htl,Apt
- | - |  |  | Level 1 | 20: (No corresponding level); 40: Level 1; 45: (No corresponding level)
- | - |  |  | Level 2 | 20: (No corresponding level); 40: Level 2; 45: (No corresponding level)
3 | 3 |  |  | ■Level 3 | 20: Satisfies the Building Standard Law.; 40: ■Level 3; 45: Satisfies the Building Standard Law.
4 | 4 |  |  | Level 4 | 20: The Building Standard Law is satisfied and building materials not regulated under the Building Standard Law (i.e. materials not included in its directives and materials with JIS/JAS F-4 star rating) are used in at least 70% of the total area of floors, walls, ceilings and attics.; 40: Level 4; 45: The Building Standard Law is satisfied and building materials not regulated under the Building Standard Law (i.e. materials not included in its directives and materials with JIS/JAS F-4 star rating) are used in at least 70% of the total area of floors, walls, ceilings and attics.
5 | 5 |  |  | Level 5 | 20: The Building Standard Law is satisfied and building materials not regulated under the Building Standard Law (i.e. materials not included in its directives and materials with JIS/JAS F-4 star rating) are used in at least 90% of the total area of floors, walls, ceilings and attics; most material used has a low level of formaldehyde and other VOC emissions.; 40: Level 5; 45: The Building Standard Law is satisfied and building materials not regulated under the Building Standard Law (i.e. materials not included in its directives and materials with JIS/JAS F-4 star rating) are used in at least 90% of the total area of floors, walls, ceilings and attics; most material used has a low level of formaldehyde and other VOC emissions.
0 | 0 |  |  | Outline of env. efforts | bar: 20
|  |  |  | 4.1.2 Asbestos | 35: <N.A.>
既存のみ評価 |  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 0; 40: Dwelling and Accommodation Areas; 55: Weighting coef.(default) =; 60: 0
|  |  |  | 0 | 20: Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt; 40: 0; 45: Hsp,Htl,Apt
1 | 1 |  |  | Level 1 | 20: レベル２を満たさない。; 40: Level 1; 45: レベル２を満たさない。
2 | 2 |  |  | Level 2 | 20: 吹き付けアスベスト等を使用しているが、封じ込め又は囲い込みが行われている。; 40: Level 2; 45: 吹き付けアスベスト等を使用しているが、封じ込め又は囲い込みが行われている。
3 | 3 |  |  | Level 3 | 20: 吹き付けアスベスト等を一切使用していない。; 40: Level 3; 45: 吹き付けアスベスト等を一切使用していない。
- | - |  |  | Level 4 | 20: (該当するレベルなし); 40: Level 4; 45: (該当するレベルなし)
- | - |  |  | Level 5 | 20: (該当するレベルなし); 40: Level 5; 45: (該当するレベルなし)
0 | 0
|  |  |  | 4.1.3 ダニ・カビ等 | 35: <N.A.>
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 0; 40: Dwelling and Accommodation Areas; 55: Weighting coef.(default) =; 60: 0
|  |  |  | 0 | 20: Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt; 30: Sch(E.S./J.H.S./H.S.); 40: 0; 45: Hsp,Htl,Apt
1 | 1 |  |  | Level 1 | 20: レベル３を満たさない。; 30: レベル３を満たさない。; 40: Level 1; 45: レベル３を満たさない。
- | - |  |  | Level 2 | 20: (該当するレベルなし); 30: (該当するレベルなし); 40: Level 2; 45: (該当するレベルなし)
3 | 3 |  |  | Level 3 | 20: 内装は、床・壁の50％以上～65％未満の面積において、ダニ・カビの発生を抑制、あるいは清掃・メンテナンスに配慮したものとなっている。; 30: ［ダニ又はダニアレルゲン］≦１００匹／㎡; 40: Level 3; 45: 内装は、床・壁の50％以上～65％未満の面積において、ダニ・カビの発生を抑制、あるいは清掃・メンテナンスに配慮したものとなっている。
4 | 4 |  |  | Level 4 | 20: 内装は、床・壁の65％以上～80％未満の面積において、ダニ・カビの発生を抑制、あるいは清掃・メンテナンスに配慮したものとなっている。; 30: (該当するレベルなし); 40: Level 4; 45: 内装は、床・壁の65％以上～80％未満の面積において、ダニ・カビの発生を抑制、あるいは清掃・メンテナンスに配慮したものとなっている。
5 | 5 |  |  | Level 5 | 20: 内装は、床・壁の80％以上の面積において、ダニ・カビの発生を抑制、あるいは清掃・メンテナンスに配慮したものとなっている。; 30: レベル３の基準に加え、定期的に掃除を行っている、などの運用面の取組を行っている。; 40: Level 5; 45: 内装は、床・壁の80％以上の面積において、ダニ・カビの発生を抑制、あるいは清掃・メンテナンスに配慮したものとなっている。
0 | 0
|  |  |  | 4.1.4 レジオネラ対策 | 35: <N.A.>
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 0; 40: Dwelling and Accommodation Areas; 55: Weighting coef.(default) =; 60: 0
|  |  |  | 0 | 20: 事・Sch・Rtl・Rst・Hal・Fct・Hsp; 40: 0; 45: Hsp,Htl,Apt
1 | 1 |  |  | Level 1 | 20: レベル３を満たさない。; 40: Level 1; 45: レベル３を満たさない。
- | - |  |  | Level 2 | 20: (該当するレベルなし); 40: Level 2; 45: (該当するレベルなし)
3 | 3 |  |  | Level 3 | 20: 冷却塔の水処理、飛散対策等が最低限施されており、給湯器も最低限の対策が施されている。; 40: Level 3; 45: 冷却塔の水処理、飛散対策等が最低限施されており、給湯器も最低限の対策が施されている。
4 | 4 |  |  | Level 4 | 20: 冷却塔がない。または、冷却塔の水処理、飛散対策等が十分に施されており、給湯器は最低限の対策が施されている。; 40: Level 4; 45: 冷却塔がない。または、冷却塔の水処理、飛散対策等が十分に施されており、給湯器は最低限の対策が施されている。
5 | 5 |  |  | Level 5 | 20: 確実な対策を行うために、レベル４を超える特別な配慮を行っている。かつ、それらの設備のメンテナンスが容易な計画となっている。; 40: Level 5; 45: 確実な対策を行うために、レベル４を超える特別な配慮を行っている。かつ、それらの設備のメンテナンスが容易な計画となっている。
0 | 0 |  |  | Outline of env. efforts | 40: 30字以内で記入
|  | 4.2 | Ventilation
4.2.1 Ventilation Rate
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 0.33333; 40: Dwelling and Accommodation Areas; 55: Weighting coef.(default) =; 60: 0
|  |  |  | 3 | 20: Off,Sch(Univ. etc.), Rtl,Rst,Hal,Hsp,Htl,Fct,Apt; 30: Sch(E.S./J.H.S./H.S.); 40: 3; 45: Hsp,Htl,Apt
1 | 1 |  |  | Level 1 | 20: Not adequate for level 3.; 30: (No corresponding level); 40: Level 1; 45: Not adequate for level 3.
- | - |  |  | Level 2 | 20: (No corresponding level); 30: (No corresponding level); 40: Level 2; 45: (No corresponding level)
3 | 3 |  |  | ■Level 3 | 20: For rooms equipped with a centrally-controlled air mixing system, a ventilation rate of 25 m3/h per person or higher; or if not centrally controlled, a ventilation rate as required in the Building Standard Law (including measures for sick house syndrome) and the Law for Maintenance of Sanitation in Buildings.; 30: Ventilation rate required in the Building Standard Law (including measures for sick house syndrome) and the School Sanitation Standards.; 40: ■Level 3; 45: For rooms equipped with a centrally-controlled air mixing system, a ventilation rate of 25 m3/h per person or higher; or if not centrally controlled, a ventilation rate required in the Building Standard Law (including measures for sick house syndrome) and the Law for Maintenance of Sanitation in Buildings.
4 | 4 |  |  | Level 4 | 20: For rooms equipped with a centrally-controlled air mixing system, a ventilation rate of 30 m3/h per person or higher; or if not centrally controlled, a ventilation rate 20% higher than required in the Building Standard Law (including measures for sick house syndrome) and the Law for Maintenance of Sanitation in Buildings.; 30: Ventilation rate that is 20% higher than required in the Building Standard Law (including measures for sick house syndrome) and the School Sanitation Standards.; 40: Level 4; 45: For rooms equipped with a centrally-controlled air mixing system, a ventilation rate of 30 m3/h per person or higher; or if not centrally controlled, a ventilation rate 20% higher than required in the Building Standard Law (including measures for sick house syndrome) and the Law for Maintenance of Sanitation in Buildings.
5 | 5 |  |  | Level 5 | 20: For rooms equipped with a centrally-controlled air mixing system, a ventilation rate of 35 m3/h per person or higher; or if not centrally controlled, a ventilation rate 40% higher than required in the Building Standard Law (including measures for sick house syndrome) and the Law for Maintenance of Sanitation in Buildings.; 30: Ventilation rate that is 40% higher than required in the Building Standard Law (including measures for sick house syndrome) and the School Sanitation Standards.; 40: Level 5; 45: For rooms equipped with a centrally-controlled air mixing system, a ventilation rate of 35 m3/h per person or higher; or if not centrally controlled, a ventilation rate 40% higher than required in the Building Standard Law (including measures for sick house syndrome) and the Law for Maintenance of Sanitation in Buildings.
0 | 0 |  |  | Outline of env. efforts | bar: 20
4.2.2 Natural Ventilation Performance
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 0.33333; 40: Dwelling and Accommodation Areas; 55: Weighting coef.(default) =; 60: 0
|  |  |  | 3 | 20: Off,Sch(Univ. etc.),Hal(Lib.),Fct; 30: Sch(E.S./J.H.S./H.S.); 40: 3; 45: Hsp,Htl; 55: Apt
1 | 1 |  |  | Level 1 | 20: Not adequate for level 3.; 30: Not adequate for level 3.; 40: Level 1; 45: Not adequate for level 3.; 55: Not adequate for level 3.
- | - |  |  | Level 2 | 20: (No corresponding level); 30: (No corresponding level); 40: Level 2; 45: (No corresponding level); 55: (No corresponding level)
3 | 3 |  |  | ■Level 3 | 20: Fixed windows and no valid opening for natural ventilation; or fixed windows and valid opening area for natural ventilation of less than 25 cm2/m2; or openable windows and valid opening area for natural ventilation of at least 1/50 of the total floor space of an occupied room.; 30: Valid opening area for natural ventilation of at least 1/20 of the total floor space of an occupied room.; 40: ■Level 3; 45: Fixed windows and no valid opening for natural ventilation; or fixed windows and valid opening area for natural ventilation of less than 50 cm2/m2; or openable windows and valid opening area for natural ventilation of at least 1/20 of the total floor space of an occupied room.; 55: Area of openable windows at least 1/10 of floor space of occupied room.
4 | 4 |  |  | Level 4 | 20: Fixed windows and valid opening area for natural ventilation of at least 25 cm2/m2; or openable windows and valid opening area for natural ventilation of at least 1/30 of the total floor space of an occupied room; or where in-room air quality improvement is expected with use of outdoor air cooling system which can use more than double the required outdoor air volume.; 30: Valid opening area for natural ventilation of at least 1/15 of the total floor space of an occupied room.; 40: Level 4; 45: Fixed windows and valid opening area for natural ventilation of at least 50 cm2/m2; or openable windows and valid opening area for natural ventilation of at least 1/15 of the total floor space of an occupied room; or where in-room air quality improvement is expected with use of outdoor air cooling system which can use more than double the required outdoor air volume.; 55: Area of openable windows at least 1/8 of floor space of occupied room.
5 | 5 |  |  | Level 5 | 20: Fixed windows and valid opening area for natural ventilation of at least 50 cm2/m2; or openable windows and valid opening area for natural ventilation of at least 1/15 of the total floor space of an occupied room; or valid opening area for natural ventilation is equivalent to Level 4, and in-room air quality improvement is expected with use of outdoor air cooling system that can use more than double the required outdoor air volume.; 30: Valid opening area for natural ventilation of at least 1/10 of the total floor space of an occupied room.; 40: Level 5; 45: Fixed windows and valid opening area for natural ventilation of at least 100 cm2/m2; or openable windows and valid opening area for natural ventilation of at least 1/10 of the total floor space of an occupied room; or valid opening area for natural ventilation is equivalent to Level 4, and in-room air quality improvement is expected with use of outdoor air cooling system that can use more than double the required outdoor air volume.; 55: Area of openable windows at least 1/6 of floor space of occupied room.
0 | 0 |  |  | Outline of env. efforts | bar: 20
[5 empty] | Valid opening area for natural ventilation |  | of the total floor area of an occupied room
4.2.3 Consideration for Outside Air Intake
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 0.33333; 40: Dwelling and Accommodation Areas; 55: Weighting coef.(default) =; 60: 0
|  |  |  | 3 | 20: Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct; 30: Apt; 40: 3; 45: Hsp,Htl; 55: Apt
1 | 1 |  |  | Level 1 | 20: Not adequate for level 3.; 30: Not adequate for level 3.; 40: Level 1; 45: Not adequate for level 3.; 55: Not adequate for level 3.
- | - |  |  | Level 2 | 20: (No corresponding level); 30: (No corresponding level); 40: Level 2; 45: (No corresponding level); 55: (No corresponding level)
3 | 3 |  |  | ■Level 3 | 20: The air intakes are oriented away from pollution sources, considering conditions in areas surrounding the site. They are also oriented away from extraction vents or positioned at least 3 m away.; 30: The air intakes are oriented away from pollution sources, considering conditions in areas surrounding the site.; 40: ■Level 3; 45: The air intakes are oriented away from pollution sources, considering conditions in areas surrounding the site. They are also oriented away from extraction vents or positioned at least 3 m away.; 55: The air intakes are oriented away from pollution sources, considering conditions in areas surrounding the site.
4 | 4 |  |  | Level 4 | 20: The air intakes are oriented away from pollution sources, considering conditions in areas surrounding the site. They are also positioned at least 6 m away from extraction vents.; 30: (No corresponding level); 40: Level 4; 45: The air intakes are oriented away from pollution sources, considering conditions in areas surrounding the site. They are also positioned at least 6 m away from extraction vents.; 55: (No corresponding level)
5 | 5 |  |  | Level 5 | 20: The air intakes are oriented away from pollution sources, considering conditions in areas surrounding the site. They are also oriented away from extraction vents and positioned at least 6 m away.; 30: The air intakes are oriented away from pollution sources, considering conditions in areas surrounding the site. They are also oriented away from extraction vents or positioned at least 3 m away.; 40: Level 5; 45: The air intakes are oriented away from pollution sources, considering conditions in areas surrounding the site. They are also oriented away from extraction vents and positioned at least 6 m away.; 55: The air intakes are oriented away from pollution sources, considering conditions in areas surrounding the site. They are also oriented away from extraction vents or positioned at least 3 m away.
0 | 0
|  |  |  | 4.2.4 給気計画 | 35: <N.A.>
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 0; 40: Dwelling and Accommodation Areas; 55: Weighting coef.(default) =; 60: 0
|  |  |  | 0 | 20: Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct; 40: 0; 45: Hsp,Htl,Apt
1 | 1 |  |  | Level 1 | 20: レベル３を満たさない。; 40: Level 1; 45: レベル３を満たさない。
- | - |  |  | Level 2 | 20: (該当するレベルなし); 40: Level 2; 45: (該当するレベルなし)
3 | 3 |  |  | Level 3 | 20: 外気が空調機でレタンと混合され各室に熱負荷から決まる風量で配分される等、各室の負荷条件によっては、必ずしも必要な場所に必要な外気量が保証されないシステムとなっている。; 40: Level 3; 45: 外気が空調機でレタンと混合され各室に熱負荷から決まる風量で配分される等、各室の負荷条件によっては、必ずしも必要な場所に必要な外気量が保証されないシステムとなっている。
- | - |  |  | Level 4 | 20: (該当するレベルなし); 40: Level 4; 45: (該当するレベルなし)
5 | 5 |  |  | Level 5 | 20: 外気がレタンと混合されず、各室の必要外気量が直接各室に供給されている等、各室の負荷条件によらず、必要な場所に必要な外気量が保証されるシステムとなっている。; 40: Level 5; 45: 外気がレタンと混合されず、各室の必要外気量が直接各室に供給されている等、各室の負荷条件によらず、必要な場所に必要な外気量が保証されるシステムとなっている。
0 | 0 |  |  | Outline of env. efforts | bar: 20
|  | 4.3 | Operation Plan
|  |  |  | 4.3.1 CO2 Monitoring | 40: 4.3.2 Control of Smoking
|  |  |  | Entire Building and Common Areas | 30: Weighting coef.(default) =; 35: 0.5; 40: Entire Building and Common Areas; 55: Weighting coef.(default) =; 60: 0.5
|  |  |  | 3 | 20: Off,Sch,Rtl,Rst,Hal,Fct; 40: 3; 45: Off,Sch,Rtl,Rst,Hal,Hsp(Waiting Room),Htl,Fct
1 | 1 |  |  | Level 1 | 20: Not adequate for level 3.; 40: Level 1; 45: Not adequate for level 3.
- | - |  |  | Level 2 | 20: (No corresponding level); 40: Level 2; 45: (No corresponding level)
3 | 3 |  |  | ■Level 3 | 20: The system is based on manual measurement, with the minimum necessary level of recording.; 40: ■Level 3; 45: There is a minimum level of measures, such as smoking booths, to avoid exposing non-smokers to smoke.
4 | - |  |  | Level 4 | 20: The system is based on manual measurement, a management manual, etc. has been provided for properly maintaining air quality, and it functions effectively.; 40: Level 4; 45: (No corresponding level)
5 | 5 |  |  | Level 5 | 20: The system has constant central monitoring of CO2. Also, a management manual, etc. has been provided for properly maintaining air quality, and it functions effectively.; 40: Level 5; 45: Smoking is confirmed to be prohibited in the entire building. Alternatively, there is an adequate level of measures, such as smoking booths, to avoid exposing non-smokers to smoke.
0 | 0 |  |  | Outline of env. efforts | 40: Outline of env. efforts
Note on H197: Max. or Ave. of all dwelling units
Note on J197: Max. or Ave. of all dwelling units
Note on L197: Max. (worst) of all dwelling units
Note on N197: Min. (worst) of all dwelling units

## Q2
[11 empty] | n Building Name | XXX Building
|  |  |  | 1 | Level 1 | ■Level 1
|  |  |  | 2 | Level 2 | ■Level 2 |  |  | プルダウン選択肢 | <N.A.> | Yes | Not apply | Preliminary design stage
|  |  |  | 3 | Level 3 | ■Level 3 | [5 empty] | Apply | Execution design stage
|  |  |  | 4 | Level 4 | ■Level 4 | [6 empty] | Construction completion stage
|  |  |  | 5 | Level 5 | ■Level 5 |  |  |  |  | Yes |  | 0
|  |  |  | 0 | Level | Level |  |  |  |  | No | 特定建築物に該当する場合の取組みで評価する
|  | Q2 Quality of Service | [5 empty] | Select from pull-down menus or enter figures and comments. |  |  |  |  | Execution design stage
The outline of efforts for environment should be filled in short if the score exceeds Level 3. If there is a lot to write, describe it on the consideration sheet.
|  | 1 | Service Ability
|  | 1.1 | Functionality & Usability
1.1.1 Provision of Space & Storage
|  |  |  | Entire Building and Common Areas |  |  | Weighting coef.(default) = | 0.33333 | Dwelling and Accommodation Areas |  |  | Weighting coef.(default) = | 0
|  |  |  | 3 | Off,Fct |  | Sch |  | 3 | Hsp |  | Htl
1 | 1 |  |  | Level 1 | Not adequate for level 3. |  |  |  | Level 1 | Not adequate for level 3. |  | Not adequate for level 3.
- | - |  |  | Level 2 | (No corresponding level) |  |  |  | Level 2 | (No corresponding level) |  | (No corresponding level)
3 | 3 |  |  | ■Level 3 | Working space per person is at least 6 m2. |  |  |  | ■Level 3 | Private rooms at least 8 m2/bed, multi-bed rooms at least 6 m2/bed. |  | Single room at least 15 m2, twin room at least 22 m2.
4 | 4 |  |  | Level 4 | Working space per person is at least 9 m2. |  |  |  | Level 4 | (No corresponding level) |  | Single room at least 22 m2, twin room at least 32 m2.
5 | 5 |  |  | Level 5 | Working space per person is at least 12 m2 |  |  |  | Level 5 | Private rooms at least 10 m2/bed, multi-bed rooms at least 8 m2/bed. |  | Single room at least 30 m2, twin room at least 40 m2.
0 | 0 |  |  | Outline of env. efforts
[5 empty] | Working space |  | Bedroom |  | Single room |  | Twin room
1.1.2 Use of Advanced Information System
|  |  |  | Entire Building and Common Areas |  |  | Weighting coef.(default) = | 0.33333 | Dwelling and Accommodation Areas |  |  | Weighting coef.(default) = | 0
|  |  |  | 3 | Off,Fct |  |  |  | 3 | Htl,Apt
1 | 1 |  |  | Level 1 | Not adequate for level 2. |  |  |  | Level 1 | Not adequate for level 2.
2 | 2 |  |  | Level 2 | Measures such as OA floors* accommodate layout changes, and electrical sockets for OA equipment have at least 30 VA/m2 socket capacity. In addition, optical fiber is routed into the building for communications. |  |  |  | Level 2 | Communications lines able to carry telephone and broadcasting are routed into each dwelling or guest room.
3 | 3 |  |  | ■Level 3 | Measures such as OA floors accommodate layout changes, and electrical sockets for OA equipment have at least 30 VA/m2 socket capacity. Also, level 2 is satisfied for communications, and communications lines with capacity for one data communications device per 8 m2 (one phone, one PC) is routed onto each floor. |  |  |  | ■Level 3 | Level 2 is satisfied, and Internet services not adequate for level 4 are provided.
4 | 4 |  |  | Level 4 | Measures such as OA floors accommodate layout changes, and electrical sockets for OA equipment have at least 40 VA/m2 socket capacity. Also, level 3 is satisfied for communications, lines for multiple communications carriers are routed into the building, and space is provided for each communications carrier to lay cables onto each floor. |  |  |  | Level 4 | Each dwelling or guest room is equipped with a communications environment able to use 100 Mbit-class broadband.
5 | 5 |  |  | Level 5 | Measures such as OA floors accommodate layout changes, and electrical sockets for OA equipment have at least 50 VA/m2 socket capacity. Also, level 4 is satisfied for communications, Gigabit communications lines are routed onto each floor, and tenant EPS is ensured for communications between floors. |  |  |  | Level 5 | Each dwelling or guest room is equipped with a communications environment able to use Gbit-class broadband.
0 | 0 |  |  | Outline of env. efforts
|  |  |  | Socket capacity |  | VA/㎡
1.1.3 Barrier-free Planning
|  |  |  | Entire Building and Common Areas |  |  | Weighting coef.(default) = | 0.33333
|  |  |  | 3 | Sch(Public E.S./ Public J.H.S),Rtl,Rst,Hal,Hsp,Htl |  |  |  | Off,Sch(Except Public E.S./Public J.H.S),Fct,Apt |  | Sch(Public E.S./ Public J.H.S),Rtl,Rst,Hal,Hsp,Htl【<2000㎡】
1 | 1 |  |  | Level 1 | Not adequate for level 3. |  |  |  | Not adequate for level 3.
- | - |  |  | Level 2 | (No corresponding level) |  |  |  | (No corresponding level)
3 | 3 |  |  | ■Level 3 | The building satisfies the standard for easing building use (the minimum level) under the Barrier-free Building Law. |  |  |  | At least half of the building satisfies the standard for easing building use (the minimum level) under the Barrier-free Building Law.
4 | 4 |  |  | Level 4 | The building satisfies the standard for easing building use (the preferred level) under the Barrier-free Building Law. |  |  |  | The building satisfies the standard for easing building use (the minimum level) under the Barrier-free Building Law.
5 | 5 |  |  | Level 5 | The building exceeds the standard for easing and guiding building use (the preferred level) under the Barrier-free Building Law, achieving the universal design level. |  |  |  | The building satisfies the standard for easing building use (the desirable level) under the Barrier-free Building Law.
0 | 0 |  |  | Outline of env. efforts
|  | 1.2 | Amenity
1.2.1 Perceived Spaciousness & Access to View
既存はOff務所のみ評価 |  |  |  | Entire Building and Common Areas |  |  | Weighting coef.(default) = | 0.33333 |  |  | Dwelling and Accommodation Areas | Weighting coef.(default) = | 0
|  |  |  | 3 | Off,Fct |  | Rtl,Rst |  | Sch(Univ.,etc) | Sch（ES/JS/JHS） | 3 | Hsp,Htl,Apt
1 | 1 |  |  | Level 1 | Not adequate for level 3. |  | Not adequate for level 3. |  | Not adequate for level 2. | Not adequate for level 3. | Level 1 | Not adequate for level 3.
2 | - |  |  | Level 2 | (No corresponding level) |  | (No corresponding level) |  | Ceiling height of at least 2.7 m in classrooms. | (No corresponding level) | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | Ceiling height of at least 2.5 m in office space and windows provide all occupants with sufficient awareness of the outside environment. |  | Ceiling height at least 3.0 m in sales area. |  | Ceiling height of at least 3.0 m in classrooms. | Ceiling height at least 2.7 m in most classrooms. | ■Level 3 | Ceiling height at least 2.3 m in Dwelling and Accommodation Area.
4 | 4 |  |  | Level 4 | Ceiling height of at least 2.7 m in office space and windows provide all occupants with sufficient awareness of the outside environment. |  | Ceiling height at least 3.3 m in sales area. |  | Ceiling height of at least 3.1 m in classrooms. | (No corresponding level) | Level 4 | Ceiling height at least 2.5 m in Dwelling and Accommodation Area.
5 | 5 |  |  | Level 5 | Ceiling height of at least 2.9 m in office space and windows provide all occupants with sufficient awareness of outside the environment. |  | Ceiling height at least 3.6 m in sales area. |  | Ceiling height of at least 3.2 m in classrooms. | Ceiling height exceeding 2.7 m in classrooms. | Level 5 | Ceiling height at least 2.7 m in Dwelling and Accommodation Area.
0 | 0 |  |  | Outline of env. efforts |  |  |  |  | Celling height |  | m
1.2.2 Space for Refreshment
|  |  |  | Entire Building and Common Areas |  |  | Weighting coef.(default) = | 0.33333
|  |  |  | 3 | Off,Fct |  |  |  |  | Rtl
- | 1 |  |  | Level 1 | (No corresponding level) |  |  |  |  | (No corresponding level)
2 | 2 |  |  | Level 2 | There is no refreshment space. |  |  |  |  | Not adequate for level 3.
3 | 3 |  |  | ■Level 3 | Refreshment space is less than 1% of the working space. |  |  |  |  | Rest space is at least 2% of the sales floor area.
4 | 4 |  |  | Level 4 | Refreshment space is at least 1% of the working space. |  |  |  |  | Rest space is at least 3% of the sales floor area
5 | 5 |  |  | Level 5 | Refreshment space accounts for at least 1% of the working space and refreshment equipment such as a vending machine is provided. |  |  |  |  | Rest space is at least 4% of the sales floor area.
0 | 0 |  |  | Outline of env. efforts | [5 empty] | Refreshment space |  | Rest space
1.2.3 Décor Planning
|  |  |  | Entire Building and Common Areas |  |  | Weighting coef.(default) = | 0.33333 | Dwelling and Accommodation Areas |  |  | Weighting coef.(default) = | 0
Min | Min |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  |  |  | 1 | Hsp,Htl,Apt
0 | 0 |  |  | Level 1 | Not adequate for level 3. |  |  |  | ■Level 1 | Not adequate for level 3.
2 | 2 |  |  | Level 2 | (No corresponding level) |  |  |  | Level 2 | (No corresponding level)
2 | 2 |  |  | ■Level 3 | Two of the efforts to be evaluated are addressed. |  |  |  | Level 3 | Two of the efforts to be evaluated are addressed.
3 | 3 |  |  | Level 4 | Three of the efforts to be evaluated are addressed. |  |  |  | Level 4 | Three of the efforts to be evaluated are addressed.
4 | 4 |  |  | Level 5 | Four of the efforts to be evaluated are addressed. |  |  |  | Level 5 | Four of the efforts to be evaluated are addressed.
|  |  |  | Outline of env. efforts |  |  |  |  | Note; Describe introduced technics for each effort.
|  |  |  | Efforts to be evaluated |  |  |  |  | Efforts to be evaluated
[5 empty] | 3 | Description |  |  |  | 1 | Description
|  |  |  | No.1 | Yes | The concept of the building as a whole is well defined, and specific efforts to reflect the concept are made at the décor planning stage. (For example, shifting to natural and ecological materials in a building with an ecological theme). |  |  | No.5 |  | The concept of the building as a whole is well defined, and specific efforts to reflect the concept are made at the décor planning stage. (For example, shifting to natural and ecological materials in a building with an ecological theme).
|  |  |  | No.2 |  | The functions required of the building have been clarified, and specific measures to encourage those functions are indicated at the décor planning stage. (For example, in Hotels and similar facilities, the interior is perceived as living space, and natural materials such as wood and stone are introduced in deliberate efforts to produce a living room-like atmosphere). |  |  | No.6 |  | The functions required of the building have been clarified, and specific measures to encourage those functions are indicated at the décor planning stage. (For example, in Hotels and similar facilities, the interior is perceived as living space, and natural materials such as wood and stone are introduced in deliberate efforts to produce a living room-like atmosphere).
|  |  |  | No.3 | Yes | Specific measures were taken during décor planning to integrate the lighting design (e.g. effective use of indirect lighting specific to activity type, décor planning in consideration of color temperatures of a light source, etc.). |  |  | No.7 |  | Specific measures were taken during décor planning to integrate the lighting design (e.g. effective use of indirect lighting specific to activity type, décor planning in consideration of color temperatures of a light source, etc.).
|  |  |  | No.4 |  | Mockups and interior perspectives are used to verify the décor planning in advance. |  |  | No.8 |  | Mockups and interior perspectives are used to verify the décor planning in advance.
|  |  |  | Total | 2 | items |  |  | Total2 | 0 | items
|  | 1.3 | Maintenance
|  |  |  | 1.3.1 Design That Considers Maintenance | [10 empty] | 1.3.1 維持管理に配慮した設計 | 1.3.1 総合的な取組み
新築 | 既存 |  |  | Entire Building and Common Areas |  |  | Weighting coef.(default) = | 0.5 |  |  |  | Floor area = | 7000
Min | Min |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Apt,Fct | [9 empty] | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Apt,Fct | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Apt,Fct
0 |  |  |  | Level 1 | (No corresponding level) | [9 empty] | (該当するレベルなし) | (該当するレベルなし)
0 |  |  |  | Level 2 | Building plan includes insufficient level of consideration of maintenance. (Not adequate for level 3.) | [9 empty] | 維持管理に配慮した設計において、取り組みにおいて該当する項目数が十分でない。（評価する取組みが 0～2） | 維持管理に配慮した設計において、取り組みにおいて該当する項目数が十分でない。（評価する取組みが 0～2）
3 |  |  |  | ■Level 3 | Building plan includes standard level of consideration of maintenance. (3-5 of the efforts to be evaluated are addressed.) | [9 empty] | 維持管理に配慮した設計において、取り組みにおいて該当する項目数が標準である。（評価する取組みが 3～5） | 維持管理に配慮した設計において、取り組みにおいて該当する項目数が標準である。（評価する取組みが 3～5）
6 |  |  |  | Level 4 | Building plan includes higher-than-standard level of consideration of maintenance. (6-8 of the efforts to be evaluated are addressed.) | [9 empty] | 維持管理に配慮した設計において、取り組みにおいて該当する項目数が標準以上である。（評価する取組みが 6～8） | 維持管理に配慮した設計において、取り組みにおいて該当する項目数が標準以上である。（評価する取組みが 6～8）
9 |  |  |  | Level 5 | Building plan includes excellent level of consideration of maintenance. (More than 9 of the efforts to be evaluated are addressed.) | [9 empty] | 維持管理に配慮した設計において、充実した取り組みにおいて該当する項目数が行われている。（評価する取組みが 9～） | 維持管理に配慮した設計において、充実した取り組みにおいて該当する項目数が行われている。（評価する取組みが 9～）
|  |  |  | Outline of env. efforts |  |  |  |  | Note; Describe introduced technics for each effort.
Efforts to be evaluated
Max | 新築 |  |  |  | 3 | Category | Description
1 |  |  |  | No.1 | Yes | I. Interior finishes | 1) Interior walls use finish methods, materials, paints or coatings that are highly dirt resistant.
1 |  |  |  | No.2 |  |  | 2) Floors use finish methods, materials, paints or coatings that are highly dirt resistant.
1 |  |  |  | No.3 |  | II. Décor design | 3) The design and structure of floors enables washing with water.
1 |  |  |  | No.4 |  |  | 4) Design of interior walls and floors avoids creating dust traps and places to leave objects.
1 |  |  |  | No.5 |  |  | 5) The first and second doors of windbreak lobbies are distanced so that they are not open at the same time, or are otherwise designed to prevent the entry of dust, etc.
1 |  |  |  | No.6 |  |  | 6) Floor materials with very different maintenance methods are not placed close together.
1 |  |  |  | No.7 | Yes | III. Exterior finishes | 7) Exterior walls and glass are designed with highly dirt resistant construction materials, or with finishes such as weather-resistant paint and hydrophilic properties.
1 |  |  |  | No.8 | Yes | IV. Facade design | 8) Exterior walls are designed to maintain clean surface conditions by preventing water pooling and wet-dry effects from rain water by using rain flashing.
1 |  |  |  | No.9 |  |  | 9) Measures have been applied to prevent damage from the droppings of birds (pigeons, crows, starlings, etc.).
1 |  |  |  | No.10 | Yes |  | 10) Metal parts exposed on the exterior are plated or otherwise treated against corrosion.
1 |  |  |  | No.11 |  | V. Décor & exterior space design | 11) Movement routes, including outdoor spaces and management areas, are designed to eliminate steps as far as possible (steps not exceeding around 5 mm).
|  |  |  | No.12 |  | VI. Other | 12) Wall-mounted urinal and urinal are adopted.
1 |  |  |  | No.13 |  |  | 13) Efforts have been made in areas other than the above, with consideration for maintenance.
|  |  |  | Total | 4 | items
1.3.1 総合的な取組み | 既存 |  |  | Ⅰ 建築Rtl衛生法における特定建築Rtlの場合に評価する取組み
Max |  |  |  |  | 3 | 評価項目 |  | 評価内容 |  |  |  |  | 評価ポイント
3 |  |  |  | No.1 | 3 | 1) 業務仕様 |  | 清掃管理および設備管理仕様書の基本方針において環境配慮を明示している。 |  |  |  |  | 3
1 |  |  |  | No.2 | 1 | 2) 契約形態 |  | 安定した品質を維持するために業務契約期間を2年以上としている。 |  |  |  |  | 1
3 |  |  |  | No.3 | 3 | 3) 業務手順 |  | 清掃管理と設備管理における業務標準手順書を用意している。 |  |  |  |  | 3
2 |  |  |  | No.4 | 0 | 4) インスペクション |  | 清掃および設備の維持管理状態のインスペクション記録がある。 |  |  |  |  | 2
1 |  |  |  | No.5 | 0 | 5) 計画 |  | 外気に接するガラス･照明の清掃を含めた計画書がある。 |  |  |  |  | 1
2 |  |  |  | No.6 | 0 | 6) 業務員への教育 |  | 年1回以上の環境等をテーマにしたトレーニングの計画と記録がある。 |  |  |  |  | 2
1 |  |  |  | No.7 | 0 | 7) EMS |  | 管理者が外部評価による環境マネジメントシステム(EMS)の認証を得ている。 |  |  |  |  | 1
|  |  |  | 合計 | 7 | 項目 | [6 empty] | 13
Ⅱ 建築Rtl衛生法における特定建築Rtlに該当しない建築Rtlの場合に評価する取組み
Max |  |  |  |  | 4 | 評価項目 |  | 評価内容 |  |  |  |  | 評価ポイント
3 |  |  |  | No.1 | 3 | 1) 頻度 |  | 施設清掃や設備点検･清掃の箇所別頻度の設定がなされている。 |  |  |  |  | 3
3 |  |  |  | No.2 | 3 | 2) 役割 |  | 施設清掃と設備点検･清掃における各責任者･委託先が決められている。 |  |  |  |  | 3
3 |  |  |  | No.3 | 3 | 3) 手順 |  | 施設清掃と設備点検･清掃における作業手順書やマニュアルを用意している。 |  |  |  |  | 3
2 |  |  |  | No.4 | 0 | 4) 点検 |  | 施設清掃と設備点検･清掃の点検記録がある。 |  |  |  |  | 2
1 |  |  |  | No.5 | 0 | 5) 実施 |  | 施設清掃や設備点検･清掃の実施記録がある。 |  |  |  |  | 1
1 |  |  |  | No.6 | 0 | 6) 共有 |  | 施設清掃と設備点検･清掃の点検結果を共有する機Halを設けている。 |  |  |  |  | 1
|  |  |  | 合計 | 9 | 項目 | [6 empty] | 13
1.3.2 Securing Maintenance Functions
新築 | 既存 |  |  | Entire Building and Common Areas |  |  | Weighting coef.(default) = | 0.5 |  | gross floor area= | 7000 | Remarks
Min | Min |  |  | 3 | Off,Sch,Rst,Rtl,Hal,Hsp,Htl,Apt,Fct
0 |  |  |  | Level 1 | (No corresponding level) | [6 empty] | Level 3 is awarded to all buildings with a gross floor area of 500 m2 or less. Note; Enter Level 3 directly if the evaluated building has a gross floor area of 500 m2 or less.
0 |  |  |  | Level 2 | Insufficient level of measures has been taken to ensure functionality of maintenance system. (0-8 of the efforts to be evaluated are addressed.)
4 |  |  |  | ■Level 3 | Standard level of measures has been taken to ensure functionality of maintenance system. (4-6 of the efforts to be evaluated are addressed.)
7 |  |  |  | Level 4 | Higher than standard level of measures has been taken to ensure functionality of maintenance system. (7-9 of the efforts to be evaluated are addressed.)
10 |  |  |  | Level 5 | Extensive level of measures has been taken to ensure functionality of maintenance system. (More than 10 of the efforts to be evaluated are addressed.)
Outline of env. efforts
Efforts to be evaluated
Max | 新築 |  |  |  | 3 | I. Specified buildings in the Law for Maintenance of Sanitation in Buildings |  |  |  | II. Non-specified buildings in the Law for Maintenance of Sanitation in Buildings
1 |  |  |  | No.1 |  | [1] Adequate space has been used for cleaning staff rooms, relative to the floor area. |  |  |  | ―
1 |  |  |  | No.2 | Yes | [2] Adequate space has been used for cleaning equipment rooms, relative to the floor area. |  |  |  | [1] Storage space for cleaning materials is included in the design.
1 |  |  |  | No.3 | Yes | [3] The cleaning equipment rooms have washing areas with drainage channels to safe drainage facilities. |  |  |  | [2] Sink for cleaning materials with safe drainage is installed. * Hospital secure, in addition to the above, a space in which washing machines for cleaning materials are installed, depending on the number of beds.
1 |  |  |  | No.4 | Yes | [4] Space is planned for washing and drying mops and rags, for the sake of hygiene. |  |  |  | [3] Areas cleaned with water (e.g. washrooms, garbage storage, kitchens) are designed with a 2% gradient.
1 |  |  |  | No.5 | Yes | [5] Adequate space has been provided for sorting waste, materials for recycling, and bulky garbage items, relative to the floor area, and an easy way to move those materials outside has been planned. |  |  |  | [4] Adequate space for waste material storage and removal is included in the design.
1 |  |  |  | No.6 |  | [6] Cleaning sinks are installed for each toilet, or for each floor. |  |  |  | [5] Dedicated sinks or water taps are installed.
1 |  |  |  | No.7 |  | [7] Cleaning equipment for each type of floor material has been anticipated, and the layout of electrical receptacles (numbers and spacings) for use in cleaning work has been planned accordingly. |  |  |  | [6] Power outlets for outside/hallway cleaning are included in the design.
1 |  |  |  | No.8 | Yes | [8] Design ensures that maintenance work can be performed safely on exterior glass and walls, air supply and vent holes, light fixtures and other fixtures in high places. |  |  |  | [7] Safety of maintenance activities in high places (e.g. exterior glass, vents, lighting fixtures) is addressed in the design.
1 |  |  |  | No.9 | Yes | [9] Suitable levels of lighting for cleaning purposes can be set. |  |  |  | [8] Water traps under all sinks in washrooms, hot water rooms, and kitchens can be removed for cleaning.
1 |  |  |  | No.10 |  | [10] Valves and other devices requiring day-to-day adjustment are installed in positions which allow convenient operation. |  |  |  | [9] Devices requiring day-to-day adjustment (e.g. valves) are installed in positions which allow convenient operation.
1 |  |  |  | No.11 |  | [11] Inspection access holes for equipment concealed in ceiling voids are of the necessary sizes for inspection. |  |  |  | [10] Inspection access holes for equipment concealed in ceiling voids are of the necessary sizes for inspection.
1 |  |  |  | No.12 |  | [12] Equipment that is not in private areas can be accessed from common areas for maintenance. |  |  |  | [11] Equipment that is not in private areas can be accessed from common areas for maintenance.
1 |  |  |  | No.13 |  | [13] Other than the above, points related to securing maintenance functions have been identified and implemented. |  |  |  | [12] Other than the above, points related to securing maintenance functions have been identified and implemented.
|  |  |  | Total | 6 | items
Sch校版 |  |  |  | （１） | 大掃除の実施 |  | 大掃除は、定期に行われていること。（毎Sch年３回）
|  |  |  | （２） | 雨水の排水溝等 |  | 屋上等の雨水排水溝に、泥や砂等が堆積していないこと。また、雨水配水管の末端は、砂や泥等により管径が縮小していないこと。（毎Sch年１回）
|  |  |  | （３） | 排水の施設・設備 |  | 汚水槽、雑排水槽等の施設・設備は、故障等がなく適切に機能していること。 （毎Sch年１回）
既存 |  |  |  | Ⅰ 建築Rtl衛生法における特定建築Rtlの場合に評価する取組み |  |  | 特定建築Rtlに該当する場合の取組みで評価する |  |  | Ⅱ 建築Rtl衛生法における特定建築Rtlに該当しない建築Rtlの場合に評価する取組み
[5 empty] | 3 | 評価項目 | 評価内容 |  |  | 評価内容 |  |  | 評価ポイント
|  |  |  | No.1 | 1 | 1) 汚染源対策 | 充分な長さのエントランスマットを設置している。(外部、内部含む5ｍ以上) |  |  | ある程度の長さのエントランスマットを設置している。 |  |  | 1
|  |  |  | No.2 | 3 | 2) 清掃方法 | ① 清掃業務において効果的な方法を採用している。 |  |  | - |  |  | 3
|  |  |  | No.3 | 0 |  | ② 清掃業務において環境影響の少ない方法を採用している。 |  |  | - |  |  | 3
|  |  |  | No.4 | 2 |  | - |  |  | ① トイレ、共用部、厨房、玄関マットは毎日、清掃を実施する事としている。 |  |  | 2
|  |  |  | No.5 | 0 |  | - |  |  | ② 希釈をする洗浄剤の希釈方法を明記している。 |  |  | 1
|  |  |  | No.6 | 0 | 3) 清掃資材 | ① 環境ラベル取得製品の採用。(エコマーク、グリーンマークなど) |  |  | ① 環境ラベル取得製品を採用している。（エコマーク、グリーンマークなど） |  |  | 1
|  |  |  | No.7 | 0 |  | ② 清掃用ケミカルのⅰ 床用保護剤、ⅱ 床用洗浄剤(カーペット含む)、ⅲ トイレ用洗浄剤、ⅳ ガラス用洗浄剤の4製品に関して、環境負荷と安全に配慮した製品を採用している。(判定表を参照) |  |  | ② 清掃資材専用の保管スペースがある。 |  |  | 2
|  |  |  | No.8 | 1 |  | - |  |  | ③ トイレ、共用部、厨房などの清掃に使用するケミカルの2種類以上についてMSDS（化SchRtl質安全データシート）を保管している。 |  |  | 1
|  |  |  | No.9 | 0 | 4) 感染症対策 | 清掃業務において感染症対策に配慮した方法を採用している。 |  |  | ① トイレ清掃では除菌剤配合洗剤を使用している。 |  |  | 1
|  |  |  | No.10 | 0 |  | - |  |  | ② 感染防止を考慮した嘔吐Rtlの処理方法がある。 |  |  | 1
|  |  |  | No.11 | 0 | 5) 安全対策 | 清掃業務において安全に配慮した方法を採用している。 |  |  | 手袋、メガネ、マスクなどの保護具の着用を促している。 |  |  | 2
|  |  |  | 合計 | 4 | ポイント
判定表
[5 empty] | 評価項目 |  | 判定基準
[5 empty] | 水素イオン濃度（pH） |  | 原液＝pH5～pH9である事。
[5 empty] | シックハウス配慮 |  | ⅰ 床用保護剤
ⅱ 床用洗浄剤 ⅲ トイレ用洗浄剤 ⅳ ガラス用洗浄剤
[5 empty] | 急性経口毒性 |  | LD50：＞2,000mg/kgである事。
[5 empty] | VOC濃度 |  | 製品が定める最も高濃度希釈時のVOC含有率が洗浄剤＜1% 床用保護剤＜7%である事。（沸点260℃未満のVOC対象）
[5 empty] | 有害性が判明している化SchRtl質 |  | 特定化SchRtl質の環境への排出量の把握等及び管理の改善の促進に関する法律（ＰＲＴＲ法）の「第一種指定化SchRtl質」と「第二種指定化SchRtl質」が指定割合以下である事。
|  |  |  | 1.3.3 Sanitation management operations |  |  |  | <N.A.>
既存 |  |  |  | Entire Building and Common Areas |  |  | Weighting coef.(default) = | 0 |  | 延床面積＝ | 7000
Min |  |  |  | 3 | 事・Sch・Rtl・Hal・Htl | [6 empty] | 備考
0 |  |  |  | Level 1 | (該当するレベルなし) | [6 empty] | 延床面積500㎡以下の建築Rtlは レベル3とする。 注）500㎡以下の建Rtlは直接入力により、レベル3を選択してください。
0 |  |  |  | Level 2 | 3つの設備管理業務の取り組みポイントで-１(ﾚﾍﾞﾙ2)の取り組みがひとつでもある場合
0 |  |  |  | ■Level 3 | 3つの設備管理業務の取り組みポイントが 0点
1 |  |  |  | Level 4 | 3つの設備管理業務の取り組みポイントが 1～2点
3 |  |  |  | Level 5 | 3つの設備管理業務の取り組みポイントが 3点
|  |  |  | Outline of env. efforts |  |  |  |  | 30字以内で記入
評価する取組み
[5 empty] | 3 | 評価項目 | 建築Rtl衛生法における特定建築Rtl |  |  | 建築Rtl衛生法における特定建築Rtlに該当しない建築Rtl |  |  | ポイント
|  |  |  | No.1 |  | Ⅰ 空調管理の評価 | 建築Rtl環境衛生管理基準の空調設備において不適切項目がある。 |  |  | 空調管理は何も実施していない。 |  |  | -1（レベル2）
0 |  |  |  | No.2 |  |  | 建築Rtl環境衛生管理基準を満たし、フィルターの定期的な点検・清掃を行っている。 |  |  | 建築基準法施行細則第8条（建築設備等の定期報告）に基づく換気設備定期点検を年1回実施し、改善している。 ※特定行政庁が規定する特殊建築Rtlに該当しない場合は取組み「0点」として評価する。 |  |  | 0
1 |  |  |  | No.3 |  |  | 建築Rtl環境衛生管理基準を満たした以上に、特別な対策を行っている。 |  |  | 建築Rtl環境衛生管理基準レベルの空調管理を実施し、記録を保管している。 |  |  | 1
|  |  |  | No.4 |  | Ⅱ ねずみ等の点検・防除の評価 | 建築Rtl環境衛生管理基準の害虫駆除において不適切項目がある。 |  |  | ねずみ等の点検・防除は何も実施していない。 |  |  | -1（レベル2）
0 |  |  |  | No.5 |  |  | 建築Rtl環境衛生管理基準を満たし、6ヶ月に1回の点検および防除を行っている。 |  |  | 各建築Rtlに適用されている法律、規則、基準などに則り、ねずみ等の点検・防除を定期的に実施している。 ※法律、規則、基準などがない建築Rtlの場合は年1回のねずみ等の点検・防除を実施している。 |  |  | 0
1 |  |  |  | No.6 |  |  | 建築Rtl環境衛生管理基準を満たした以上に、特別な対策を行っている。 |  |  | 建築Rtl環境衛生管理基準レベルのねずみ等の点検・防除を実施し、記録を保管している。 |  |  | 1
|  |  |  | No.7 |  | Ⅲ 給水・給湯管理 （Rst用・炊事用・浴用等）の評価 | 建築Rtl環境衛生管理基準の給水設備において不適切項目がある。 |  |  | 給水・給湯管理（Rst用・炊事用・浴用等）は何も実施していない。 |  |  | -1（レベル2）
0 |  |  |  | No.8 |  |  | 建築Rtl環境衛生管理基準を満たしている。 |  |  | 「水道法」に基づき、受水槽の清掃や水質の外部検査を年1回実施し、改善している。 ※直結式給水で受水槽がない場合は取組み「0点」として評価する。 |  |  | 0
1 |  |  |  | No.9 |  |  | 建築Rtl環境衛生管理基準を満たした以上に、特別な対策を行っている。 |  |  | 建築Rtl環境衛生管理基準レベルの給水・給湯管理（Rst用・炊事用・浴用等）を実施し、記録を保管している。 |  |  | 1
|  |  |  | 合計 | 0 | ポイント |  | -１(ﾚﾍﾞﾙ2)の取組み＝ | 0 |  |  |  | 3
|  | 2 | Durability & Reliability
|  | 2.1 | Earthquake Resistance, Seismic Isolation, Seismic Control, & Vibration Control
|  |  |  | 2.1.1 Earthquake-resistance (Resistance to building breakage) |  |  |  |  | 2.1.2 Seismic Isolation, Seismic & Vibration Control (Internal Equipment Protection)
[7 empty] | Weighting coef.(default) = | 0.8 |  |  |  | Weighting coef.(default) = | 0.2
|  |  |  | 3 | Off,Sch(Univ. etc.),Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  | Sch(E.S./J.H.S./H.S.) |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
- | - |  |  | Level 1 | (No corresponding level) |  | (No corresponding level) |  | Level 1 | (No corresponding level)
2 | - |  |  | Level 2 | (No corresponding level) |  | The building's earthquake resistance meets the requirements of the Building Standard Law. |  | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | The building's earthquake resistance meets the requirements of the Building Standard Law. |  | The building's earthquake resistance exceeds the requirements of the Building Standard Law by a 25% margin. |  | ■Level 3 | No device to suppress shaking is used.
4 | 4 |  |  | Level 4 | The building's earthquake resistance exceeds the requirements of the Building Standard Law by a 25% margin. |  | (No corresponding level) |  | Level 4 | A device to suppress shaking has been introduced, and internal equipment is partially protected in the event of an earthquake or strong wind.
5 | 5 |  |  | Level 5 | The building's earthquake resistance exceeds the requirements of the Building Standard Law by a 50% margin. Alternatively, damage control design has been used. |  | The building's earthquake resistance exceeds the requirements of the Building Standard Law by a 50% margin. Alternatively, damage control design has been used. |  | Level 5 | A seismic isolation system is used.
0 | 0 |  |  | Outline of env. efforts |  |  |  |  | Outline of env. efforts
|  | 2.2 | Service Life of Components
|  |  |  | 2.2.1 Service Life of Structural Materials |  |  |  |  | 2.2.2 Necessary Refurbishment Interval for Exterior Finishes
[7 empty] | Weighting coef.(default) = | 0.2 |  |  |  | Weighting coef.(default) = | 0.2
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
- | 1 |  |  | Level 1 | (No corresponding level) |  |  |  | Level 1 | Less than 10 years
- | 2 |  |  | Level 2 | (No corresponding level) |  |  |  | Level 2 | 10 years or more, less than 20 years
3 | 3 |  |  | ■Level 3 | Level equivalent to Grade 1 of “3-1. Durability Grade (Structural Frame, etc.)” in the Japan Housing Performance Indication Standards |  |  |  | ■Level 3 | 20 years
4 | 4 |  |  | Level 4 | Level equivalent to Grade 2 of “3-1. Durability Grade (Structural Frame, etc.)” in the Japan Housing Performance Indication Standards |  |  |  | Level 4 | 21 years or more, less than 30 years
5 | 5 |  |  | Level 5 | Level equivalent to Grade 3 of “3-1. Durability Grade (Structural Frame, etc.)” in the Japan Housing Performance Indication Standards |  |  |  | Level 5 | 30 years or more
0 | 0 |  |  | Outline of env. efforts |  |  |  |  | Outline of env. efforts
|  |  |  | Expected lifespan |  | yr. | Note: Describe water-cement ratio, cover thickness, rust prevention measures (steel structure), etc. |  | Expected necessary interval |  | years | Note; Describe major materials etc.
|  |  |  | 2.2.3 Necessary Renewal Interval for Main Interior Finishes |  |  |  |  | 2.2.4 Necessary Renewal Interval for Air Conditioning and Ventilation Ducts
[7 empty] | Weighting coef.(default) = | 0.1 |  |  |  | Weighting coef.(default) = | 0.1
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct |  | Apt |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
1 | - |  |  | Level 1 | Less than 5 years |  | Less than 10 years |  | Level 1 | (No corresponding level)
2 | - |  |  | Level 2 | 5 years or more, less than 10 years |  | 10 years or more, less than 15 years |  | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | 10 years |  | 15 years |  | ■Level 3 | Zinc-plated steel sheet used almost throughout.
4 | 4 |  |  | Level 4 | 11 years or more, less than 20 years |  | 16 years or more, less than 25 years |  | Level 4 | Exposed exterior ducts, kitchen venting ducts, high-humidity venting ducts and similar applications that would have shorter service lives than other applications when made from zinc-plated steel sheet are made from stainless steel or Galvalume to extend service life. Alternatively, appropriate provision has been made for drainage of internal condensation.
5 | 5 |  |  | Level 5 | 20 year or more |  | 25 years or more |  | Level 5 | At least 90% of exposed exterior ducts, kitchen venting ducts, high-humidity venting ducts and similar applications that would have shorter service lives than other applications when made from zinc-plated steel sheet are made from stainless steel or Galvalume to extend service life.
0 | 0 |  |  | Outline of env. efforts |  |  |  |  | Outline of env. efforts
|  |  |  | Expected necessary interval |  | years | Note; Describe major materials etc. |  |  | Note; Describe major materials etc.
|  |  |  | 2.2.5 Necessary Renewal Interval for HVAC and Water Supply and Drainage Pipes |  |  |  |  | 2.2.6 Necessary Replacement Interval for Major Equipment and Services
[7 empty] | Weighting coef.(default) = | 0.2 |  |  |  | Weighting coef.(default) = | 0.2
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
- | 1 |  |  | Level 1 | (No corresponding level) |  |  |  | Level 1 | Less than 7 years
- | 2 |  |  | Level 2 | (No corresponding level) |  |  |  | Level 2 | 7 years or more, less than 15 years
3 | 3 |  |  | ■Level 3 | D or better used in almost all the top three main building types. |  |  |  | ■Level 3 | 15 years
4 | 4 |  |  | Level 4 | C or better used in at least two of the top three main building types. |  |  |  | Level 4 | 16 years or more, less than 30 years
5 | 5 |  |  | Level 5 | B or better used in at least two of the top three main building types, and E is not used. |  |  |  | Level 5 | 30 years or more
0 | 0 |  |  | Outline of env. efforts |  |  |  |  | Outline of env. efforts
[5 empty] | Note; Describe major materials etc. |  |  |  | Expected necessary interval |  | years
既存で評価 |  | 2.3 | Appropriate Renewal |  |  |  |  | <N.A.>
既存で評価 |  |  |  | 2.3.1 屋上（屋根）・外壁仕上げ材の更新 |  |  |  | <N.A.> | 2.3.2 配管・配線材の更新 |  |  |  | <N.A.>
|  |  |  | Entire Building and Common Areas |  |  | Weighting coef.(default) = | 0 | Entire Building and Common Areas |  |  | Weighting coef.(default) = | 0
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
1 | 1 |  |  | Level 1 | メンテナンス記録がなく判定不可能。 |  |  |  | Level 1 | メンテナンス記録がなく判定不可能。
2 | 2 |  |  | Level 2 | 全て耐用年数を超えている。 |  |  |  | Level 2 | 全て耐用年数を超えている。
3 | 3 |  |  | ■Level 3 | 主要機器は耐用年数以内である。 |  |  |  | ■Level 3 | 主要機器は耐用年数以内である。
- | - |  |  | Level 4 | (該当するレベルなし) |  |  |  | Level 4 | (該当するレベルなし)
5 | 5 |  |  | Level 5 | 全て耐用年数以内である。 |  |  |  | Level 5 | 全て耐用年数以内である。
0 | 0 |  |  | Outline of env. efforts |  |  |  |  | Outline of env. efforts |  |  |  |  | 30字以内で記入
既存で評価 |  |  |  | 2.3.3 主要設備機器の更新 |  |  |  | <N.A.>
|  |  |  | Entire Building and Common Areas |  |  | Weighting coef.(default) = | 0
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
1 | 1 |  |  | Level 1 | メンテナンス記録がなく判定不可能。
2 | 2 |  |  | Level 2 | 全て耐用年数を超えている。
3 | 3 |  |  | ■Level 3 | 主要機器は耐用年数以内である。
- | 4 |  |  | Level 4 | (該当するレベルなし)
5 | 5 |  |  | Level 5 | 全て耐用年数以内である。
0 | 0 |  |  | Outline of env. efforts |  |  |  |  | 30字以内で記入
|  | 2.4 | Reliability
2.4.1 HVAC System
>=2k | [6 empty] | Weighting coef.(default) = | 0.2
Min | Min |  |  | 3 | 【>=2000㎡】Off,Hal,Hsp,Htl,Fct |  | 7000 | 【>=2000㎡】Sch,Rtl,Rst,Apt |  | 0 | 【<2000㎡】 |  | 0
0 | 0 |  |  | Level 1 | Not adequate for Level 3. |  |  | Not adequate for Level 3. |  |  | (No corresponding level)
1 | 1 |  |  | Level 2 | (No corresponding level) |  |  | (No corresponding level) |  |  | (No corresponding level)
1 | 1 |  |  | ■Level 3 | One of the efforts to be evaluated is addressed. Alternatively, there is no centralized HVAC system. |  |  | One of the efforts to be evaluated is addressed. Alternatively, there is no centralized HVAC system. |  |  | Not adequate for Level 4.
2 | 2 |  |  | Level 4 | Two of the efforts to be evaluated are addressed. |  |  | (No corresponding level) |  |  | One of the efforts to be evaluated is addressed.
3 | 2 |  |  | Level 5 | More than three of the efforts to be evaluated are addressed. |  |  | More than two of the efforts to be evaluated are addressed. |  |  | More than two of the efforts to be evaluated are addressed.
|  |  |  | Outline of env. efforts |  |  |  |  | Note; Describe introduced technics for each effort.
| <2k |  |  | Efforts to be evaluated
| Min |  |  |  | 3 | Description
| 0 |  |  | No.1 |  | Buildings with no centrally-controlled HVAC system
| 0 |  |  | No.2 | Yes | 1) Circuits are divided according to the importance of their ventilation equipment, and more important circuits are given priority in operation after a disaster. Also, ways of running the ventilation with reduced load capacity have been examined.
| 0 |  |  | No.3 |  | 2) Dispersion and duplication of heat source types (electricity, gas, etc.), with backups.
| 1 |  |  | No.4 |  | 3) Countermeasures (such as suspended pipes) have been taken to ensure that overall function can continue even when the building is partially damaged by an earthquake.
| 2 |  |  | No.5 |  | 4) Circuits are divided according to the importance of their air conditioning equipment, and more important circuits are given priority in operation after a disaster. Also, ways of running the air conditioning with reduced load capacity have been examined.
|  |  |  | Total | 1 | items | 【>=2000㎡】 | Off,Hal,Hsp, Htl,Fct | 3 | Sch,Rtl, Rst,Apt | 3 | 【<2000㎡】 | 4
2.4.2 Water Supply & Drainage
[7 empty] | Weighting coef.(default) = | 0.2
Min | Min |  |  | 3 | Off,Sch,Hal,Hsp,Htl,Fct,Apt |  |  | 7000 | Rtl,Rst |  |  | 0
0 | 0 |  |  | Level 1 | Not adequate for Level 2. |  |  |  | Not adequate for Level 2.
1 | 1 |  |  | Level 2 | One of the efforts to be evaluated is addressed. |  |  |  | One of the efforts to be evaluated is addressed.
2 | 2 |  |  | ■Level 3 | Two of the efforts to be evaluated are addressed. |  |  |  | Two of the efforts to be evaluated are addressed.
3 | 3 |  |  | Level 4 | Three of the efforts to be evaluated are addressed. |  |  |  | (No corresponding level)
4 | 3 |  |  | Level 5 | More than four of the efforts to be evaluated are addressed. |  |  |  | More than three of the efforts to be evaluated are addressed.
Outline of env. efforts
Efforts to be evaluated
[5 empty] | 3 | Description
|  |  |  | No.1 | Yes | Water-saving equipment is used.
|  |  |  | No.2 |  | This is limited to cases where it is used on a majority of the installed equipment. Water-saving devices are those approved as Eco Mark products, or those equivalent to water-saving equipment that is the approval standard for Eco Mark products (Toilet bowls: approx. 6 L/use, urinals: approx. 4 L/use).
|  |  |  | No.3 |  | Plumbing systems are separated as far as possible to reduce the portions that become unserviceable in the event of a disaster.
|  |  |  | No.4 |  | The building has a pit for temporary waste water storage, in case mains sewerage is unavailable after a disaster.
|  |  |  | No.5 |  | The building has two separate tanks, one for water reception and one elevated tank.
|  |  |  | No.6 | Yes | Planning enables the use of well water, gray water, etc.
|  |  |  | No.7 |  | The building is equipped with a simple filtration system allowing conversion of rain water to potable water in the event of a disaster (Not applied to Rtl and Rst).
|  |  |  | Total |  | Off,Sch,Hal,Hsp,Htl,Fct,Apt: | 2 | items | 3 | Rtl,Rst: | 1 | items | 2
2.4.3 Electrical Equipment
[7 empty] | Weighting coef.(default) = | 0.2
Min | Min |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  |  | 7000 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt 【<2000㎡】 |  |  | 0
0 | 0 |  |  | Level 1 | Not adequate for Level 3. |  |  |  | (No corresponding level)
1 | 0 |  |  | Level 2 | (No corresponding level) |  |  |  | (No corresponding level)
1 | 0 |  |  | ■Level 3 | One or two of the efforts to be evaluated are addressed. |  |  |  | Not adequate for Level 4.
3 | 1 |  |  | Level 4 | Three of the efforts to be evaluated are addressed. |  |  |  | One of the efforts to be evaluated is addressed.
4 | 2 |  |  | Level 5 | More than four of the efforts to be evaluated are addressed. |  |  |  | More than two of the efforts to be evaluated are addressed.
Outline of env. efforts
Efforts to be evaluated
[5 empty] | 3 | Description
|  |  |  | No.1 |  | 1) Emergency generator is installed.
|  |  |  | No.2 |  | 2) Uninterruptible power supply system is installed
|  |  |  | No.3 | Yes | 3) Redundant power receiving system for key service equipment is installed.
|  |  |  | No.4 |  | {Not applicable to buildings with a total floor space of less than 2,000 m2} 4) Measures described in Item A and B below have been established in order to avoid power outages or damage to data network caused by flooding in power supply equipment or precision machinery (in apartments, circuit breakers, distribution boards, etc.), or Item C applies. A. Power supply equipment and precision machinery are not installed below ground level. B. Water blocking devices (e.g. waterproof doors and panels, raised mounds, dry ditches) and drainage system (e.g. pumps, etc.) are installed to prevent flooding below ground level. C. No danger of flooding.
|  |  |  | No.5 | Yes | 5) Wiring is installed for lighting and other equipment available when connected to a power-supply car.
|  |  |  | No.6 |  | 6) Power supply is secured from two different substations.
|  |  |  | Total |  | 【>=2000㎡】 | 2 | items | 3 | 【<2000㎡】 | 2 | items | 5
2.4.4 Support Method of Machines & Ducts
[7 empty] | Weighting coef.(default) = | 0.2
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
1 |  |  |  | Level 1 | Not adequate for level 3.
- |  |  |  | Level 2 | (No corresponding level)
3 |  |  |  | ■Level 3 | Earthquake resistance class B (Human safety is assured and secondary damage prevented after a major earthquake). Or, the design lateral seismic coefficient KH is more than 1.0 after conducting the dynamic analysis.
4 |  |  |  | Level 4 | Earthquake resistance class A (In addition to Class B, important functions can be secured without major repairs). Or, the design lateral seismic coefficient KH is more than 1.5 after conducting the dynamic analysis.
5 |  |  |  | Level 5 | Earthquake resistance class S (In addition to Class A, all functions can be secured without major repairs). Or, the design lateral seismic coefficient KH is more than 2.0 after conducting the dynamic analysis.
0 | 0 |  |  | Outline of env. efforts
2.4.5 Communications & IT Equipment
[7 empty] | Weighting coef.(default) = | 0.2
Min |  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
0 |  |  |  | Level 1 | Not adequate for Level 2.
1 |  |  |  | Level 2 | One of the efforts to be evaluated is addressed.
2 |  |  |  | ■Level 3 | Two of the efforts to be evaluated are addressed.
3 |  |  |  | Level 4 | Three of the efforts to be evaluated are addressed.
4 |  |  |  | Level 5 | More than four of the efforts to be evaluated are addressed.
|  |  |  | Outline of env. efforts |  |  |  |  | Note; Describe introduced technics for each effort.
Efforts to be evaluated
[5 empty] | 3 | Description
|  |  |  | No.1 |  | 1) Communications methods are diversified, using optical fiber cable, metal cable, cellular telephone network, PHS network and others.
|  |  |  | No.2 | Yes | 2) Connections are made from two telephone exchanges to secure two communications links.
|  |  |  | No.3 |  | Countermeasures Item A and B below have been taken or Item C applies, in order to avoid damage to data networks due to water percolation into precision machinery (main wiring such as MDF and optical fiber Ethernet). A. Installation of precision machinery below ground is avoided. B. Devices to prevent the groundwater percolation (waterproof doors, waterproof panels, embankments, dry ditches) and drainage equipment (pumps, etc.) are installed. C. No danger of water percolation.
|  |  |  | No.4 | Yes | Communicative measures prioritized in case of a disaster have been taken, or community emergency radio systems are installed.
|  |  |  | No.5 |  | Disaster information is available through a cable TV or other channels in the event of a disaster.
|  |  |  | No.6 |  | An uninterruptible power supply system is installed for network devices.
|  |  |  | Total | 2 | items
|  | 3 | Flexibility & Adaptability
|  | 3.1 | Spatial Margin
3.1.1 Allowance for Floor-to-floor Height
|  |  |  | Entire Building and Common Areas |  |  | Weighting coef.(default) = | 0.6 | Dwelling and Accommodation Areas |  |  | Weighting coef.(default) = | 0
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hsp,Fct |  | Off,Sch,Rtl,Rst,Hsp,Fct [<2000m2] |  | 3 | Hsp,Htl |  | Apt
1 | 1 |  |  | Level 1 | Less than 3.3 m |  | Less than 3.1 m |  | Level 1 | Less than 3.3 m |  | Less than 2.7 m
2 | 2 |  |  | Level 2 | 3.3 m or more, less than 3.5 m |  | 3.1 m or more, less than 3.3 m |  | Level 2 | 3.3 m or more, less than 3.5 m |  | 2.7 m or more, less than 2.8 m
3 | 3 |  |  | ■Level 3 | 3.5 m or more, less than 3.7 m |  | 3.3 m or more, less than 3.5 m |  | ■Level 3 | 3.5 m or more, less than 3.7 m |  | 2.8 m or more, less than 2.9 m
4 | 4 |  |  | Level 4 | 3.7 m or more, less than 3.9 m |  | 3.5 m or more, less than 3.7 m |  | Level 4 | 3.7 m or more, less than 3.9 m |  | 2.9 m or more, less than 3.0 m
5 | 5 |  |  | Level 5 | 3.9 m or more |  | 3.7 m or more |  | Level 5 | 3.9 m or more |  | 3.0 m or more
0 | 0 |  |  | Outline of env. efforts
|  |  |  | Floor height |  | m
3.1.2 Flexibility in Floor Layout
|  |  |  | Entire Building and Common Areas |  |  | Weighting coef.(default) = | 0.4 | Dwelling and Accommodation Areas |  |  | Weighting coef.(default) = | 0
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Fct |  |  |  | 3 | Hsp,Htl,Apt
1 | 1 |  |  | Level 1 | 0.7 ≦ [Wall length/area ratio] |  |  |  | Level 1 | 0.7 ≦ [Wall length/area ratio]
2 | 2 |  |  | Level 2 | 0.5 ≦ [Wall length/area ratio] < 0.7 |  |  |  | Level 2 | 0.5 ≦ [Wall length/area ratio] < 0.7
3 | 3 |  |  | ■Level 3 | 0.3 ≦ [Wall length/area ratio] < 0.5 |  |  |  | ■Level 3 | 0.3 ≦ [Wall length/area ratio] < 0.5
4 | 4 |  |  | Level 4 | 0.1 ≦ [Wall length/area ratio] < 0.3 |  |  |  | Level 4 | 0.1 ≦ [Wall length/area ratio] < 0.3
5 | 5 |  |  | Level 5 | [Wall length/area ratio] < 0.1 |  |  |  | Level 5 | [Wall length/area ratio] < 0.1
0 | 0 |  |  | Outline of env. efforts
|  |  |  | Wall length/area ratio |  | ＝ | Length of perimeter walls [m] + length of bearing walls [m]
Exclusive area [m2]
|  | 3.2 | Floor Load Margin
|  |  |  | Entire Building and Common Areas |  |  | Weighting coef.(default) = | 0.3 |  |  | Dwelling and Accommodation Areas | Weighting coef.(default) = | 0
|  |  |  | 3 | Off,Rtl,Rst,Hal(fixed sheets),Hsp,Fct |  | Hal(unfixed sheets) |  | Sch |  | 3 | Hsp,Htl,Apt
- | - |  |  | Level 1 | (No corresponding level) |  | (No corresponding level) |  | (No corresponding level) |  | Level 1 | (No corresponding level)
2 | 2 |  |  | Level 2 | Less than 2,900 N/m2 |  | Less than 3,500 N/m2 |  | Less than 2,300 N/m2 |  | Level 2 | Less than 1,800 N/m2
3 | 3 |  |  | ■Level 3 | 2,900 N/m2 or more, less than 3,500 N/m2 |  | 3,500 N/m2 or more, less than 4,200 N/m2 |  | 2,300 N/m2 or more, less than 2,900 N/m2 |  | ■Level 3 | 1,800 N/m2 or more, less than 2,100 N/m2
4 | 4 |  |  | Level 4 | 3,500 N/m2 or more, less than 4,500 N/m2 |  | 4,200 N/m2 or more, less than 5,200 N/m2 |  | 2,900 N/m2 or more, less than 3,500 N/m2 |  | Level 4 | 2,100 N/m2 or more, less than 2,900 N/m2
5 | 5 |  |  | Level 5 | 4,500 N/m2 or more |  | 5,200 N/m2 or more |  | 3,500 N/m2 or more |  | Level 5 | 2,900 N/m2 or more
0 | 0 |  |  | Outline of env. efforts
|  |  |  | Floor Load |  | N/m2
|  | 3.3 | System Renewability
|  |  |  | 3.3.1 Ease of Air Conditioning Duct Renewal |  |  |  |  | 3.3.2 Ease of Water Supply and Drain Pipe Renewal
[7 empty] | Weighting coef.(default) = | 0.2 |  |  |  | Weighting coef.(default) = | 0.2
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
1 | 1 |  |  | Level 1 | Air conditioning ducts cannot be replaced or repaired without damaging structural elements. |  |  |  | Level 1 | Repair and replacement are not possible without damaging structural elements and finishes.
2 | 2 |  |  | Level 2 | In some cases the air conditioning ducts can be replaced or repaired without damaging structural elements, if spare sleeves are used, but that method cannot be applied to all ducts. |  |  |  | Level 2 | Repairs can be made without damaging structural elements, but replacements cannot.
3 | 3 |  |  | ■Level 3 | Space and routes for future use (future replacement work) have been provided, so that nearly all air conditioning ducts can be replaced or repaired without damaging structural elements. Alternatively, there is no central air conditioning equipment. |  |  |  | ■Level 3 | Repairs can be made without damaging structural elements and finishes, but replacements cannot.
4 | 4 |  |  | Level 4 | Exterior air conditioning ducts are used or ceiling space provided so that ducts can be replaced or repaired without damaging either structural elements or surface finishes. |  |  |  | Level 4 | Repairs and replacements can be made without damaging structural elements.
5 | 5 |  |  | Level 5 | ISS, equipment floor installation or other measures allow easy replacement or repair of air conditioning ducts without damaging surface finishes. |  |  |  | Level 5 | Repair and replacement are possible without damaging structural elements or finishes.
0 | 0 |  |  | Outline of env. efforts |  |  |  |  | Outline of env. efforts
|  |  |  | 3.3.3 Ease of Electrical Wiring Renewal |  |  |  |  | 3.3.4 Ease of Communications Cable Renewal
[7 empty] | Weighting coef.(default) = | 0.1 |  |  |  | Weighting coef.(default) = | 0.1
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
1 | 1 |  |  | Level 1 | Wiring cannot be replaced or repaired without damaging structural elements. |  |  |  | Level 1 | Communications cables cannot be replaced or repaired without damaging structural elements.
- | - |  |  | Level 2 | (No corresponding level) |  |  |  | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | Wiring can be replaced or repaired without damaging structural elements. |  |  |  | ■Level 3 | Communications cables can be replaced or repaired without damaging structural elements.
- | - |  |  | Level 4 | (No corresponding level) |  |  |  | Level 4 | (No corresponding level)
5 | 5 |  |  | Level 5 | Wiring can be replaced or repaired without damaging structural elements or surface finishes. |  |  |  | Level 5 | Communications cables can be replaced or repaired without damaging structural elements or surface finishes.
0 | 0 |  |  | Outline of env. efforts |  |  |  |  | Outline of env. efforts
|  |  |  | 3.3.5 Ease of Equipment Renewal |  |  |  |  | 3.3.6 Provision of Backup Space
[7 empty] | Weighting coef.(default) = | 0.2 |  |  |  | Weighting coef.(default) = | 0.2
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
1 | - |  |  | Level 1 | No machine hatches or routes to accommodate replacement of major service equipment are provided, and building functions cannot be maintained through replacement and repair. |  |  |  | Level 1 | (No corresponding level)
- | - |  |  | Level 2 | (No corresponding level) |  |  |  | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | Machine hatches or routes to accommodate replacement of major service equipment are provided, but building functions cannot be maintained through replacement and repair. |  |  |  | ■Level 3 | There is no planned provision of space for backup equipment.
4 | 4 |  |  | Level 4 | A temporary space to accommodate replacement of major service equipment is secured, and building functions can be maintained through replacement and repair. |  |  |  | Level 4 | There is planned provision of space for backup equipment.
5 | - |  |  | Level 5 | Machine hatches or routes to accommodate replacement of major service equipment are provided, and building functions can be maintained through replacement and repair. |  |  |  | Level 5 | (No corresponding level)
0 | 0 |  |  | Outline of env. efforts |  |  |  |  | Outline of env. efforts

## Q3
[11 empty] | n Building Name | XXX Building
|  |  |  | 1 | Level 1 | ■Level 1
|  |  |  | 2 | Level 2 | ■Level 2 |  |  | プルダウン選択肢 | <N.A.> | Yes | Not apply | Preliminary design stage
|  |  |  | 3 | Level 3 | ■Level 3 |  |  |  | 0 |  | Apply | Execution design stage
|  |  |  | 4 | Level 4 | ■Level 4 |  |  |  | 1 |  |  | Construction completion stage
|  |  |  | 5 | Level 5 | ■Level 5 |  |  |  | 2 | Yes
|  |  |  | 0 | Level | Level |  |  |  |  | No
|  | Q3 Outdoor Environment on Site | [5 empty] | Select from pull-down menus or enter figures and comments. |  |  |  |  | Execution design stage
The outline of efforts for environment should be filled in short if the score exceeds Level 3. If there is a lot to write, describe it on the consideration sheet.
|  | 1 | Preservation & Creation of Biotope
[6 empty] | Weighting coef.(default) = |  | 0.3
Min |  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
0 |  |  |  | Level 1 | No consideration has been given to the conservation and creation of habitat, and efforts are inadequate. (0-3 points in total)
4 |  |  |  | Level 2 | Some consideration has been given to the conservation and creation of habitat, but efforts are still somewhat inadequate. (4-6 points in total)
7 |  |  |  | ■Level 3 | Consideration has been given to the conservation and creation of habitat, and a standard level of efforts are being carried out. (7-9 points in total)
10 |  |  |  | Level 4 | Consideration has been given to the conservation and creation of habitat, and a relatively high level of efforts are being carried out. (10-12 points in total)
13 |  |  |  | Level 5 | Thorough consideration has been given to the conservation and creation of habitat, and a high level of efforts have been carried out. (13 or more points in total)
|  |  |  | Outline of env. efforts |  |  |  |  | Note; Describe specific initiatives for each effort.
|  |  |  | Exterior Planting Index | #DIV/0! | #DIV/0! |  | Floor areas [㎡]: |  | Exterior area |  | Construction area | 4000
|  |  |  | Building Planting Index | 0% | 0% |  |  |  | Horizontal projection areas of medium and tall trees |  | Roof planting
[10 empty] | Low trees and ground cover |  | Wall planting
Efforts to be evaluated
Max |  |  |  |  | 3 | Assessment Item |  | Description |  |  |  |  | Point allocation
2 | 既存はなし |  |  | No.1 |  | I. Identification of local characteristics and biotope plan policy |  | 1) Local characteristics of the site and surrounding areas regarding habitat are identified and an appropriate biotope plan policy has been established |  |  |  |  | 2
2 |  |  |  | No.2 | 2 | II. Conservation and restoration of biological resources |  | 1) Biological resources on site are protected or restored (e.g. flora and fauna, topsoil, wetland area composition) |  |  |  |  | 2
[8 empty] | 2) Inapplicable under CASBEE-BD/NC |  |  |  |  | ―
3 |  |  |  | No.3 |  | lll. Securing the amount of greenery |  | 1) Landscaping of exterior is carried out on a scale that Exterior planting index is measured at; |  |  |  |  | 1～3
[8 empty] | -10% or more but less than 20% and mid/high trees are planted. (1 point) -20% or more but less than 50%. (2 points) -50% or more. (3 points) |  |  |  | #DIV/0!
2 |  |  |  | No.4 |  |  |  | 2) Building planting is carried out on a scale that Building planting index is measured at; |  |  |  |  | 1～2
[8 empty] | -0.05 or higher but less than 0.2. (1 point) -0.2 or higher. (2 points) |  |  |  | Building Planting Index =0%
1 |  |  |  | No.5 | 1 | IV. Quality of Green Space |  | 1)Appropriate measures are taken against invasive species that adversely affect the ecosystems of Japan and local communities. |  |  |  |  | 1
1 |  |  |  | No.6 | 1 |  |  | 2) The greenery plan facilitates conservation of native/local species. |  |  |  |  | 1
1 |  |  |  | No.7 | 1 |  |  | 3) The greenery plan is appropriate for site and building characteristics. |  |  |  |  | 1
1 |  |  |  | No.8 |  |  |  | 4) The greenery plan facilitates conservation of natural areas inhabited by small animals. |  |  |  |  | 1
1 |  |  |  | No.9 | 1 | V Management and use of habita |  | 1) Equipment necessary for the maintenance of green areas at the building operation stage have been installed, and management policies have been established. |  |  |  |  | 1
[8 empty] | 2) Inapplicable under CASBEE-BD/NC |  |  |  |  | ―
[8 empty] | 3) Inapplicable under CASBEE-BD/NC |  |  |  |  | ―
1 |  |  |  | No.10 | 1 |  |  | 4) An environment and facilities have been provided in which building users and local people can encounter living creatures and enjoy nature. |  |  |  |  | 1
1 |  |  |  | No.11 |  | VI. Other |  | Other initiatives (State specific initiatives in the outline of env. efforts.) |  |  |  |  | 1
|  |  |  | Total | 7 | points | [6 empty] | 16
|  | 2 | Townscape & Landscape
[6 empty] | Weighting coef.(default) = |  | 0.4
Min |  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
0 |  |  |  | Level 1 | Not adequate for Level 2. (0 points in total)
1 |  |  |  | Level 2 | Sufficient level of measures for the surrounding landscape have not established. (1-2 points in total)
3 |  |  |  | ■Level 3 | Sufficient level of measures for the surrounding landscape have been established. (3 points in total)
4 |  |  |  | Level 4 | More than the sufficient level of measures for the surrounding landscape have been established. (4 points in total)
5 |  |  |  | Level 5 | Extensive level of measures for the surrounding landscape have been established. (5 or more points in total. Or the building has won local landscape-related awards.)
|  |  |  | Outline of env. efforts |  |  |  |  | Note; State the award in case of Level 5. Describe specific initiatives for each effort.
[1] Evaluate level three if the building is almost entirely unseen from public spaces, or if there is no way to give consideration to urban context and scenery. [2] Evaluate efforts based on the locally applied rules, such as urban context guidelines, etc., if any. [3] Evaluate level five if scenery is clearly stated as a reason for winning a local scenery prize, or any similar situation indicating the building has gained a certain level of positive assessment.
Efforts to be evaluated
Max |  |  |  |  | 3 | Assessment Item |  | Description |  |  |  |  | Point allocation
2 |  |  |  | No.1 | 2 | 1) Integration with surrounding landscape through positioning and design of the building |  | Building features are designed in harmony with surrounding landscape (i.e. height, wall positions, color and form of exterior finish, roof, eaves, openings fences, etc.). |  |  |  |  | 2
1 |  |  |  | No.2 | 1 | 2) Use of green space to enhance landscape |  | Aesthetic landscape is created by the building's green space. |  |  |  |  | 1
1 |  |  |  | No.3 |  | 3) Conservation of historic landscape |  | Historic landscape is maintained through conservation, restoration or recreation of the exterior of historic buildings and the existing natural environment the area. |  |  |  |  | 1
1 |  |  |  | No.4 |  | 4) Use of local materials to enhance landscape |  | Locally-significant materials are used in the building exterior to create aesthetic landscape. |  |  |  |  | 1
1 |  |  |  | No.5 |  | 5) Aesthetics from main viewpoints of surrounding area |  | Aesthetic panoramic view of the building and surrounding areas is offered from nearby parks and gathering space or distant viewpoints. |  |  |  |  | 1
1 |  |  |  | No.6 |  | 6) Other |  | Other initiatives (State specific initiatives in the outline of env. efforts.) |  |  |  |  | 1
|  |  |  | Total | 3 | points | [6 empty] | 7
|  | 3 | Local Characteristics & Outdoor Amenity
|  | 3.1 | Attention to Local Character & Improvement of Comfort
[6 empty] | Weighting coef.(default) = |  | 0.5
Min | 既存は式修正 |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
0 |  |  |  | Level 1 | No efforts have been made for local characteristics and outdoor amenity. (0 points in total)
1 |  |  |  | Level 2 | Efforts based on local characteristics and outdoor amenity are inadequate. (1 point in total)
2 |  |  |  | ■Level 3 | Efforts based on local characteristics and outdoor amenity are at a standard level. (2-3 points in total)
4 |  |  |  | Level 4 | Efforts based on local characteristics and outdoor amenity are at a relatively high level. (4 points in total)
5 |  |  |  | Level 5 | Efforts based on local characteristics and outdoor amenity are thorough and extensive. (5 or more points in total)
|  |  |  | Outline of env. efforts |  |  |  |  | Note; Describe specific initiatives for each effort.
Efforts to be evaluated
Max |  |  |  |  | 3 | Assessment Item |  | Description |  |  |  |  | Point allocation
1 |  |  |  | No.1 | 1 | I. Continuation of unique local character, history and culture |  | 1) Conservation of historic built spaces etc. |  |  |  |  | 1
Historic interior and exterior spaces building remains preserved, restored or regenerated, contributing to local culture. (Do not evaluate if measures here overlap with areas evaluated under urban context and scenery.)
1 |  |  |  | No.2 |  |  |  | 2) Use of locally-significant materials |  |  |  |  | 1
Local materials are partially used in the building's structure, interior finishes or exterior space. (Do not include measures evaluated under the local landscape section.)
1 |  |  |  | No.3 | 1 | II. Local contribution by provision of spaces, facilities and functions |  | 1) Local contribution by provision of space |  |  |  |  | 1
Structural measures such as provision of alcoves, piloti and eaves are used to provide amenity for people using urban spaces, in the form of places to shelter from rain or wait for people.
Or, space is provided in plazas, paths and side streets to provide amenity for people using the local area, in the form of rest areas and similar spaces.
1 |  |  |  | No.4 |  |  |  | 2） Local contribution by provision of facilities and functions |  |  |  |  | 1
Part of the building is equipped to provide public facilities and functions, such as meeting rooms, community halls and exhibition spaces, community centers, and community use of schools, contributing to greater activity in the community.
1 |  |  |  | No.5 |  | III. Formation of rich intermediate zones linking the building interior and exterior |  | 1） Formation of rich intermediate zones linking the building interior and exterior |  |  |  |  | 1
Open spaces that allow the passage of wind and light, such as courtyards, terraces, balconies, sun rooms, roofed plazas, light and air voids, and atria are skillfully linked to interior spaces.
Or, in areas where private and public spaces intersect, such as around entrances and balconies, light and air voids, flower beds, pergolas, deep balconies and similar elements have been built to form rich intermediate spaces which give a lived-in atmosphere.
1 |  |  |  | No.6 |  | IV. Consideration for crime prevention |  | 1） Consideration for crime prevention |  |  |  |  | 1
Crime prevention performance is considered, so that in spaces outside the building, such as plazas, trees are placed to avoid blocking lines of sight, nocturnal lighting and security cameras are installed, windows are placed where they will be useful for crime prevention, and other measures are used.
Or, if there are no plazas or pedestrian walkways, consideration is given to crime prevention in the form of avoiding the creation of blind spots, such as blind alleys and paths out of lines of sight, placing windows where they will be useful for crime prevention, and other measures.
Or, if there are boundary barriers around the site, crime and disaster prevention are considered, in the form of fences or low hedges which afford clear lines of sight, rather than continuous walls or similar barriers which block lines of sight.
新築はなし |  |  |  |  | 0 | V 屋外施設等の適切な維持管理（植栽管理を除く） |  | 7) 屋外施設等の適切な維持管理の実施 屋外施設等（舗装・ファニチャー等）について適切な維持管理（清掃・洗浄・補修等）が実施されている。 |  |  |  |  | 1
1 |  |  |  | No.7 |  | V. Participation of building users etc. |  | 1）Participation of building users etc. |  |  |  |  | 1
User satisfaction assessments (POE) are used to involve building users in the design process for cooperative housing etc. Or, residents and occupants work directly on plant management and cleaning activities and formulate operation plans, and are otherwise participating in the maintenance of the building.
[6 empty] | VI. Appropriate maintenance and management of outdoor facilities, etc. |  | 1) Inapplicable under CASBEE-BD/NC |  |  |  |  | ―
1 |  |  |  | No.8 |  | VII Other |  | Other initiatives (State specific initiatives in the outline of env. efforts.) |  |  |  |  | 1
|  |  |  | Total | 2 | points | [6 empty] | 8
|  | 3.2 | Improvement of the Thermal Environment on Site
[7 empty] | Weighting coef.(default) = | 0.5
Min |  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
0 |  |  |  | Level 1 | 0 points in total from the table of the efforts to be evaluated.
1 |  |  |  | Level 2 | 1-5 points in total from the table of the efforts to be evaluated.
6 |  |  |  | ■Level 3 | 6-11 points in total from the table of the efforts to be evaluated.
12 |  |  |  | Level 4 | 12-17 points in total from the table of the efforts to be evaluated.
18 |  |  |  | Level 5 | 18 points or more in total from the table of the efforts to be evaluated.
|  |  |  | Outline of env. efforts |  |  |  |  | Note; Describe specific initiatives for each effort.
|  |  |  | Open space | ratio
|  |  |  | Percentage of |  |  | Countermeasure area ratio | Green cover ratio | Water /evaporative surface ratio | Retroreflective surface ratio | Horizontal projection area ratio of medium and tall trees | Horizontal projection area ratio of piloti, eaves, pergolas, etc. | Paved surface ratio
|  |  |  | horizontal projection areas |  | 0% | 0% |  |  |  | 0% | 0%
|  |  |  | appropriate ground surface |  | 0% | 0% | 0% | 0% |  | 0%
|  |  |  | paved surface |  | 0% | 0% | [5 empty] | 0%
|  |  |  | appropriate exterior wall surface |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[7 empty] | subtotal area | green area | water /evaporative material covered area | retroreflective material covered area | horizontal projection areas of medium and tall trees | horizontal projection areas of piloti, eaves, pergolas, etc. | Paved area
[5 empty] | Areas [㎡] | ground surface | 5000 | 0 |  |  | 0
[6 empty] | exterior wall |  | 0
Efforts to be evaluated
Max |  |  |  |  | 3 | Assessment Item |  | Description |  |  |  |  | Point allocation
2 |  |  |  | No.1 | 2 | I . Guide wind into pedestrian areas, etc. on the site to relieve the thermal environment |  | 1) The planned form and layout of buildings guides wind onto the plot. |  |  |  |  | 2
3 |  |  |  | No.2 |  |  |  | 2) Secure paths for air movement by providing green spaces of lawn, meadow and bushes etc., and suitable spaces and paths within the plot. |  |  |  |  | 1～3
[8 empty] | Open space ratio is 40% or more, less than 60% (1 point) 60% or more, less than 80% (2 points) 80% or more (3 points) |  |  |  | Open space =0%
3 |  |  |  | No.3 |  | II. Shaded spaces are created during the summer to alleviate thermal impact on pedestrian areas on the site |  | 1) Shaded areas are created with the use of medium/tall trees, piloti, eaves, pergolas, or other similar measures. |  |  |  |  | 1～3
[8 empty] | Rate of horizontal projection area of medium and tall trees, piloti, etc. is 10% or more, less than 20% (1 point) 20% or more, less than 30% (2 points) 30% or more (3 points) |  |  |  | Countermeasure area ratio=0%
3 |  |  |  | No.4 |  | III. Shaded spaces are created during the summer to alleviate thermal impact on pedestrian areas on the site |  | 1)Surface and near-surface temperatures are controlled by establishing green and water spaces. |  |  |  |  | 1～3
[8 empty] | Total rate of green-covered areas, water-covered areas and horizontal projection areas of medium and tall trees is 10% or more, less than 20% (1 point) 20% or more, less than 30% (2 points) 30% or more (3 points) |  |  |  | Countermeasure area ratio=0%
3 |  |  |  | No.5 |  |  |  | 2)Endeavor to reduce the area of paving on the plot. |  |  |  |  | 1～3
[8 empty] | Percentage of paved area is 20% or more, less than 30% (1 point) 10% or more, less than 20% (2 points) Less than 10% (3 points) |  |  |  | Countermeasure area ratio=0%
3 |  |  |  | No.6 | 2 | IV. Exterior finishes of the building promote alleviation of thermal impact on pedestrian areas on the site |  | 1) The green space plan includes accessible rooftop areas (including artificial base). |  |  |  |  | 2～3
The building has an accessible rooftop area that is partially covered with plants. (2 points) The building has an accessible rooftop area that is extensively covered with plants. (3 points)
3 |  |  |  | No.7 |  |  |  | 2) Appropriate exterior wall materials for thermal control are used. |  |  |  |  | 1～3
[8 empty] | Percentage of exterior walls with appropriate materials is Less than 10% (1 point) 10% or more, less than 20% (2 points) 20% or more (3 points) |  |  |  | #DIV/0!
2 |  |  |  | No.8 | 2 | V. Heat vents for service equipment are appropriately located to alleviate thermal impact on pedestrian areas on the site |  | 1)Heat vents for main service equipment (e.g. air conditioning system) are installed in high locations. |  |  |  |  | 1～2
At least half of cooling towers or outdoor units generating waste heat are installed 10 meters or higher above ground level. (1 point) Most cooling towers or outdoor units generating waste heat are installed 10 meters or higher above ground level OR no units are installed. (2 points)
2 |  |  |  | No.9 |  |  |  | 2)High-temperature heat vents for main service equipment (e.g. combustion equipment) are installed in high locations. |  |  |  |  | 1～2
At least half of high-temperature heat venting units are installed 10 meters or higher above ground level. (1 point) Most high-temperature heat venting units are installed 10 meters or higher above ground level OR no units are installed. (2 points)
|  |  |  | Total | 6 | points | [6 empty] | 24
Note on I114: Site area

## LR1
[11 empty] | n Building Name | XXX Building
|  |  |  | 1 | Level 1 | ■Level 1
|  |  |  | 2 | Level 2 | ■Level 2 |  |  | プルダウン選択肢 | <N.A.> | Yes | Not apply | Preliminary design stage
|  |  |  | 3 | Level 3 | ■Level 3 | [5 empty] | Apply | Execution design stage
|  |  |  | 4 | Level 4 | ■Level 4 | [6 empty] | Construction completion stage
|  |  |  | 5 | Level 5 | ■Level 5 |  |  |  |  | Yes
|  |  |  | 0 | Level | Level |  |  |  |  | No
|  | LR1 Energy | [5 empty] | Select from pull-down menus or enter figures and comments. |  |  |  |  | Execution design stage
The outline of efforts for environment should be filled in short if the score exceeds Level 3. If there is a lot to write, describe it on the consideration sheet.
|  | 1 | Control of Heat Load on Building Envelopes
Sch校版基準 | [6 empty] | Weighting coef.(default) = | 0.3
0 |  |  |  | 3 | 小中Sch校
- | 1 |  |  |  | 一般地域 |  | 寒冷地域 |  | 暑熱地域
2 | 3 |  |  | Level 1 | (該当するレベルなし) |  | (該当するレベルなし) |  | (該当するレベルなし)
3 | 3 |  |  | Level 2 | レベル３に満たない |  | レベル３に満たない |  | レベル３に満たない
4 | 4 |  |  | ■Level 3 | 厚さが20mm以上の吹付け硬質ｳﾚﾀﾝﾌｫｰﾑ断熱材その他これに相当する断熱性能を使用し、且つ複層ガラスを使用している |  | 厚さが40mm以上の吹付け硬質ｳﾚﾀﾝﾌｫｰﾑ断熱材その他これに相当する断熱性能を使用し、且つ複層ガラスを使用している |  | 熱反ガラスを使用し、且つ水平庇１．０ｍ以上が計画されている。又は、高性能熱反ガラスを使用し、かつ水平庇0.5～1.0ｍが計画されている。
5 | 5 |  |  | Level 4 | 厚さが20mm以上の吹付け硬質ｳﾚﾀﾝﾌｫｰﾑ断熱材その他これに相当する断熱性能を使用し、且つ低放射複層ガラスを使用している |  | 厚さが40mm以上の吹付け硬質ｳﾚﾀﾝﾌｫｰﾑ断熱材その他これに相当する断熱性能を使用し、且つ低放射複層ガラスを使用している |  | 高性能熱反ガラスを使用し、且つ水平庇１．０ｍ以上が計画されている。
0 | 0 |  |  | Level 5 | レベル４に加え、ダブルスキン等の断熱に有効な手法が採用されている。 |  | レベル４に加え、ダブルスキン等の断熱に有効な手法が採用されている。 |  | レベル４に加え、外ルーバー等の日射遮蔽に有効な手法が採用されている。
|  |  |  | Entire Bldg. |  |  | Weighting coef.(default) = | 0.2
|  |  |  | 3 | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct |  |  | 7000 | 1 |  |  | 0
[6 empty] | Zones 1-7 |  | Zone 8 |  |  | Apt
1 | 1 |  |  | Level 1 | Level 1 | Level 1: [BPI][BPIm] ≧ 1.03 Level 2: [BPI][BPIm] ＝ 1.00 Level 3: [BPI][BPIm] ＝ 0.97 Level 4: [BPI][BPIm] ＝ 0.90 Level 5: [BPI][BPIm] ≦ 0.80 Between each level, it is evaluated by linear interpolation to the first decimal place. |  | Level 1: [BPI][BPIm] ≧ 1.03 Level 2: [BPI][BPIm] ＝ 1.00 Level 3: [BPI][BPIm] ＝ 0.97 Level 4: [BPI][BPIm] ＝ 0.93 Level 5: [BPI][BPIm] ≦ 0.85 Between each level, it is evaluated by linear interpolation to the first decimal place. |  | ■Level 1 | Not adequate for Level 2.
2 | 2 |  |  | Level 2 | Level 2 |  |  |  |  | Level 2 | Requirements for Grade 3 in 5-1 Thermal Insulation Performance Grade of the Japan Housing Performance Indication Standard are satisfied.
3 | 3 |  |  | ■Level 3 | ■Level 3 |  |  |  |  | Level 3 | Requirements for Grade 4 in 5-1 Thermal Insulation Performance Grade of the Japan Housing Performance Indication Standard are satisfied.
4 | 4 |  |  | Level 4 | Level 4 |  |  |  |  | Level 4 | Requirements for Grade 5 in 5-1 Thermal Insulation Performance Grade of the Japan Housing Performance Indication Standard are satisfied.
5 | 5 |  |  | Level 5 | Level 5 |  |  |  |  | Level 5 | Requirements for Grade 6 or above in 5-1 Thermal Insulation Performance Grade of the Japan Housing Performance Indication Standard are satisfied.
0 | 0 |  |  | Outline of env. efforts |  |  |  |  | Note; Present calculation methods, etc. State if average UA of entire building is used.
※ 運用期間が1年未満の場合、直接入力により対象外を選択します。
|  | 2 | Natural Energy Utilization (Direct Use)
[7 empty] | Weighting coef.(default) = | 0.1
|  |  |  | 3 | 3 | Off,Sch (Univ., etc.),Rtl,Rst,Hal,Hsp,Htl,Fct |  | 7000 | Remarks | 3 | Sch(E.S./J.H.S./H.S.),Apt |  | 0
- | - |  |  | Level 1 | Level 1 | (No corresponding level) |  |  |  | Level 1 | (No corresponding level)
- | 2 |  |  | Level 2 | Level 2 | (No corresponding level) |  |  |  | Level 2 | Natural lighting and ventilation do not meet level 3.
3 | 3 |  |  | ■Level 3 | ■Level 3 | No measures of the assessment criteria are implemented. |  |  |  | ■Level 3 | Nearly all (at least 80%) of dwelling units or classrooms face exterior walls on two sides, ensuring effective natural lighting and ventilation.
4 | 4 |  |  | Level 4 | Level 4 | Although some methods are used, their effectiveness, however, has not been examined. (Monuments, etc.) |  |  |  | Level 4 | In addition to level 3, building measures, such as ventilation voids, have been used to enhance efficacy. They influence a majority of dwelling units or classrooms (50% or more) of the building.
5 | 5 |  |  | Level 5 | Level 5 | In some of the methods used as part of the efforts subject to the assessment, their effectiveness has been confirmed. And they influence a majority of major chambers (more than 50%) of the building. |  |  |  | Level 5 | The above building measures cover most of dwelling units or classrooms (more than 80%) of the building.
0 | 0 |  |  | Outline of env. efforts |  |  |  |  | Note; Describe other initiatives. Describe architectural innovations and their impact for evaluation of Sch & Apt (if Level 4 or higher).
※ 運用期間が1年未満の場合、直接入力により対象外を選択します。
[5 empty] | % of impact |  |  |  | % of classrooms w/ adequate natural light |  |  | % of dwellings w/ adequate natural light
[9 empty] | % of classrooms w/ adequate ventilation |  |  | % of dwellings w/ adequate ventilation
Efforts to be evaluated
[6 empty] | Item | Description |  |  | Adopted Methods (effectiveness reviewed)
|  |  |  | No.1 |  | 1. Use of natural light | Planning for natural light systems that use daylight in place of lighting equipment. |  |  |  | Light shelves
|  |  |  | No.2 | [6 empty] | Top lights
|  |  |  | No.3 | [6 empty] | High side lights
|  |  |  | No.4 | [6 empty] | Other initiatives (State specific initiatives in the outline of env. efforts.)
|  |  |  | No.5 |  | 2. Use of natural ventilation | Planning for the use of natural ventilation and ventilation systems that are effective in replacing the use of air conditioning equipment and reducing cooling loads. |  |  |  | Automatic dampers, manually operated openings and windows (those with a plan for an operational management method)
|  |  |  | No.6 | [6 empty] | Night purging
|  |  |  | No.7 | [6 empty] | Ventilation systems linked to atrium
|  |  |  | No.8 | [6 empty] | Solar chimney ventilation towers
|  |  |  | No.9 | [6 empty] | Openings in two or more directions
|  |  |  | No.10 | [6 empty] | Other initiatives (State specific initiatives in the outline of env. efforts.)
|  |  |  | No.11 |  | 3. Use of geothermal energy | Planning for the use of geothermal heat usage systems that are effective in replacing the use of heat sources and air conditioning equipment and reducing heating and cooling loads. |  |  |  | Cool and heat tubes and pits
|  |  |  | No.12 | [6 empty] | Other initiatives (State specific initiatives in the outline of env. efforts.)
|  |  |  | No.13 |  | 4. Other | Planning for the effective use of nature in other systems. |  |  |  | Other initiatives (State specific initiatives in the outline of env. efforts.)
|  |  |  | Total | 0 | items
|  | 3 | Efficiency in Building Service System
|  | 3.1 | 設計仕様に基づく評価
|  |  |  | Entire Bldg. | 【Non Apt】 | [6 empty] | Weighting coef.(default) = | 0.5
|  |  |  | 5 | 5 | Non-Apt |  |  | 7000 | Remarks
|  |  |  | Level 1 | Level 1 |  | [BEI][BEIm] ≧ | 0.9 | (1.1) | see ( ) for small buildings <300m2
|  |  |  | Level 2 | Level 2 |  | [BEI][BEIm] ＝ | 0.8 | (1.0) | Equivalent to Energy Efficiency Standards
|  |  |  | Level 3 | Level 3 |  | [BEI*][BEIm*] ＝ | 0.6 |  | Equivalent to Certification Standards
|  |  |  | Level 4 | Level 4 | [BEI][BEIm] ＝ 0.5, and [BEI*][BEIm*] ≦ 0.5 |  |  |  | Equivalent to ZEB Ready
|  |  |  | ■Level 5 | ■Level 5 | [BEI][BEIm] ≦ 0.25, and [BEI*][BEIm*] ≦ 0.5 |  |  |  | Equivalent to Nearly ZEB
[6 empty] | Or, [BEI+] ≦ 0.25, and [BEI*] ≦ 0.5, and [BEI]＜[BEI*] |  |  |  | Applied only when the evaluation of off-site renewable energy is conducted (not applied when Model Building Method is used)
[6 empty] | Off,Sch | 7000 | Rtl,Htl | 0 | Rst,Hal,Hsp | 0 | Fct | 0
[5 empty] | Level 1 | [BEI][BEIm] ≧ 0.9（1.1）
[5 empty] | Level 2 | [BEI][BEIm] ＝ 0.8（1.0） |  | [BEI][BEIm] ＝ 0.8（1.0） |  | [BEI][BEIm] ＝ 0.85（1.0） |  | [BEI][BEIm] ＝ 0.75（1.0）
[5 empty] | Level 3 | [BEI*][BEIm*] ＝ 0.6 |  | [BEI*][BEIm*] ＝ 0.7 |  | [BEI*][BEIm*] ＝ 0.7 |  | [BEI*][BEIm*] ＝ 0.6
[5 empty] | Level 4 | [BEI][BEIm] ＝ 0.5, and [BEI*][BEIm*] ≦ 0.5
[5 empty] | Level 5 | [BEI][BEIm] ≦ 0.25, and [BEI*][BEIm*] ≦ 0.5
Or, [BEI+] ≦ 0.25, and [BEI*] ≦ 0.5, and [BEI]＜[BEI*]
[5 empty] | 0 | Apt |  |  | 0 | Remarks
[5 empty] | Level 1 | Primary Energy Consumption Reduction Rate (renewable energy excluded) ≦ -10％ |  |  |  | No stars on Labeling for Energy Efficiency Performance
[5 empty] | Level 2 | Primary Energy Consumption Reduction Rate (renewable energy excluded) = 0％ |  |  |  | ★ Labeling for Energy Efficiency Performance
[5 empty] | Level 3 | Primary Energy Consumption Reduction Rate (renewable energy excluded) =10％ |  |  |  | ★★ Labeling for Energy Efficiency Performance
[5 empty] | Level 4 | Primary Energy Consumption Reduction Rate (renewable energy excluded) ≧20％ |  |  |  | ★★★ Labeling for Energy Efficiency Performance Equivalent to ZEH (ZEH-M Oriented)
[5 empty] | Level 5 | Primary Energy Consumption Reduction Rate (renewable energy excluded) ≧20％, and Primary Energy Consumption Reduction Rate (renewable energy included) ≧50% |  |  |  | Equivalent to ZEH-M Ready
[6 empty] | Primary Energy Consumption Reduction Rate (renewable energy excluded) ≧30％ |  |  |  | Applicable only for buildings of more than 6 floors or when effect of introducing renewable energy is low due to reasons such as shade. ★★★★ Labeling for Energy Efficiency Performance
|  |  |  | Outline of env. efforts |  |  |  |  | Note; In addition to environmental considerations, describe the calculation method and compliance status with ZEB/ZEH, BELS, etc.
[6 empty] | Solar power generation |  | kW Solar heat |  | kW Battery |  | kWh
※ 運用期間が1年未満の場合、[BEI][BEIm]を[BEITC]と読み替えて評価します。
3.2 実績値を用いた総合評価
（１） 設計仕様に基づく評価の補正
|  |  |  | #NAME? | [3.1a、3.1bによる設備システムの高効率化のスコア]が2.0点未満 |  |  |  | 1
[5 empty] | [3,1a、3.1bによる設備システムの高効率化のスコア]が2.0点以上 |  |  |  | スコア-1.0
（２） 実測結果に基づく評価
|  |  |  | #NAME? | （１）によるスコア | 加点あり | 上下なし | 減点あり
[5 empty] | 1.0以上1.5未満 | 2 | 1 | 1
[5 empty] | 1.5以上2.0未満 | 2.5 | 1.5 | 1
[5 empty] | 2.0以上2.5未満 | 3 | 2 | 1
[5 empty] | 2.5以上3.0未満 | 3.5 | 2.5 | 1.5
[5 empty] | 3.0以上3.5未満 | 4 | 3 | 2
[5 empty] | 3.5以上4.0未満 | 4.5 | 3.5 | 2.5
[5 empty] | 4 | 5 | 4 | 3
3.1 空調設備
Sch校版基準 |  |  |  | 基本設計段階 |  |  | Weighting coef.(default) = | 0.5
0 |  |  |  | 0 | 小中Sch校 | [6 empty] | 備考
- | 1 |  |  |  | (該当するレベルなし)
2 | 3 |  |  |  | レベル３に満たない
3 | 3 |  |  |  | 冷暖房平均COPが1.25以上の熱源機器を採用
4 | 4 |  |  |  | レベル３に加え、空調対象面積の50％以上に全熱交換器を採用
5 | 5 |  |  |  | レベル４に加え、地中熱や井水、太陽熱、顕熱潜熱分離等の更なる効率化が図られている。
0 | 0
|  |  |  | 3.2 換気設備 |  | <評価しない>
3.3 照明設備
Sch校版基準 |  |  |  | 基本設計段階 |  |  | Weighting coef.(default) = | 0.5
0 |  |  |  | 0 | 小中Sch校 | [6 empty] | 備考
- | 1 |  |  |  | (該当するレベルなし) | [6 empty] | ＜７種類の制御方式＞ カード・センサー等による在室検知制御、明るさ感知による自動点滅制御、適正照度制御（初期照度補正）、タイムスケジュール制御、昼光利用照明制御、ゾーニング制御、局所制御
2 | 3 |  |  |  | レベル３に満たない
3 | 3 |  |  |  | Hf(高周波点灯専用型）が採用されている。
4 | 4 |  |  |  | レベル３に加え、７種類のうち２種類以上採用されている。
5 | 5 |  |  |  | レベル３に加え、７種類のうち４種類以上採用されている。
0 | 0
|  |  |  | 3.4 給湯設備 |  | <評価しない>
|  |  |  | 3.5 昇降機設備 |  | <評価しない>
|  | 4 | Initiatives for Efficient Operation
|  | 4.1 | Monitoring
[7 empty] | Weighting coef.(default) = | 0.4 |  |  |  | Weighting coef.(default) = | 0
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct |  |  |  | 3 | Apt
- | - |  |  | Level 1 | (No corresponding level) |  |  |  | Level 1 | (No corresponding level)
2 | - |  |  | Level 2 | It must be possible to identify the annual consumption of each kind of energy used in the building and use the base unit for energy consumption*1, or other means, for benchmark comparison. |  |  |  | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | In addition to level 2, the breakdown of energy consumption by major application*2 does not meet the requirements of Level 4 (1/4~1/2 of the total breakdown) or the system efficiency*3 evaluation does not meet the requirements of Level 5 (2~3 types). |  |  |  | ■Level 3 | No efforts to be evaluated.
4 | 4 |  |  | Level 4 | In addition to level 3, the breakdown of energy consumption by major application*2 must be identified, trends in consumption identified and analyzed, and their appropriateness confirmed. |  |  |  | Level 4 | Equipment that indicates the amount of energy consumed, environmental-load-reducing devices and the like, are employed.
5 | 5 |  |  | Level 5 | In addition to level 4, the system efficiency*3 of major equipment systems must be evaluated in order to evaluate the performance of the systems. |  |  |  | Level 5 | A system for managing energy is established and efforts for reducing energy consumption are made therein.
0 | 0 |  |  | Outline of env. efforts |  |  |  |  | Outline of env. efforts
*1 Annual primary energy consumption per floor area by building type based on statistical data, etc.
*2 Broadly, monitoring must be planned which will be able to identify the breakdown, by application, of a majority of the total energy consumption. The breakdown shall include items such as heat sources, air conditioning power, lighting and outlets, and hot water supply, which have a large breakdown ratio of annual primary energy consumption.
*3 Efficiency assessment must be performed on at least four of the types listed in the table (see commentary). If there are many systems, such as air conditioning, lighting and ventilation, it is permissible to estimate the whole from the assessment of representative systems. It must be possible to compare the energy-saving effects of introducing various methods, using the COP of heat source systems, system COP (of compound equipment), the WTF of pumped conveyance and the ATF of air movement. if district heating and cooling has been introduced, it is possible to evaluate according to a well-defined system COP, so evaluating efficiency is sufficient. Furthermore, data obtained by devices with control sensors can also be used in the efficiency assessment.
Table: Efficiency Assessment Examples
|  |  |  | Equipment Item |  | Assessment Item |  | Assessment Summary
|  |  |  | 1 | Heat source equipment | Heat source machine COP assessment |  | Amount of generated heat/energy consumed by the heat source (based on primary energy)
[6 empty] | COP assessment of heat source systems |  | Amount of generated heat/energy consumed by the heat source and related equipment (based on primary energy)
[6 empty] | Heating medium conveyance WTF |  | Amount of heat carried/energy consumed by pump (based on secondary energy)
|  |  |  | 2 | Air conditioning equipment | Air conditioner conveyance ATF |  | Amount of heat carried/energy consumed by fan (based on secondary energy)
[6 empty] | Total enthalpy heat exchange effect |  | Amount of heat reduced, amount of energy
[6 empty] | Cooling effect by external air |  | Amount of heat reduced, amount of energy
[6 empty] | Multi-COP assessment for buildings |  | Efficiency in multi-split A/C system
|  |  |  | 3 | Ventilation equipment | Assessment of variable air volume control |  | Reduced energy consumption through CO concentration control, temperature control, etc.
|  |  |  | 4 | Lighting equipment | Assessment of various types of control |  | Amount of energy saved by the use of daylight, occupant sensors, etc.
|  |  |  | 5 | Hot water supply equipment | Heat source machine COP assessment |  | Amount of generated heat/energy consumed by the heat source (based on primary energy)
[6 empty] | COP assessment of heat source systems |  | Amount of generated heat/energy consumed by the heat source and related equipment (based on primary energy)
[6 empty] | Heating medium transmission WTF |  | Amount of heat carried/energy consumed by pump (based on secondary energy)
|  |  |  | 6 | Elevator | Individual control operation effect |  | Reduced energy
|  |  |  | 7 | Other | Assessment of solar power generation facility |  | Power generation efficiency/Rating efficiency/Annual efficiency
[6 empty] | Heat storage tank |  | Efficiency of heat storage tank
[6 empty] | CGS assessment |  | Electricity generation efficiency, overall efficiency, energy saving rate
[6 empty] | Coordinated controls |  | Lighting/ventilation on/off control linked with security sensors
[6 empty] | Other |  | A/C CO2 control effect, Ventilation CO2 control effect, Task ambient A/C effect, Task ambient lighting effect, etc.
|  | 4.2 | Operation & Management System
[7 empty] | Weighting coef.(default) = | 0.4 |  |  |  | Weighting coef.(default) = | 0
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct |  |  |  | 3 | Apt
1 | 1 |  |  | Level 1 | No operation and management have been planned. |  |  |  | Level 1 | No efforts to be evaluated.
2 | - |  |  | Level 2 | Organizations, systems or management policies have been planned for operation and management. |  |  |  | Level 2 | (No corresponding level)
3 | 3 |  |  | Level 3 | In addition to level 2, there must be an organized operation and management system, designated manager. |  |  |  | ■Level 3 | User manuals for individual facilities are provided to the occupants.
4 | 4 |  |  | Level 4 | In addition to level 3, target values for energy consumption in the whole buildings have been planned and presented to the building owner, based on calculation of annual energy consumption. |  |  |  | Level 4 | In addition to satisfying the requirements for Level 3, general instructions regarding an energy-saving way of living are given to the occupants.
5 | 5 |  |  | Level 5 | In addition to level 4, there must be regular verification of equipment performance during building operation, with specific actions planned for repair of malfunctions etc. (commissioning system) |  |  |  | Level 5 | In addition to satisfying the requirements for Level 3, appropriate instructions regarding the facilities and specifications installed in the subject dwelling unit, suitable for the respective building and life style, are given to the occupants.
0 | 0 |  |  | Outline of env. efforts |  |  |  |  | Outline of env. efforts
|  | 4.3 | Expanding adoption of non-fossil energy
[7 empty] | Weighting coef.(default) = | 0.1
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct | [6 empty] | Remarks
- | - |  |  | Level 1 | (No corresponding level) | [6 empty] | Select N.A. if any of the followings are not applied; 1) On-site renewable energy facilities or off-site renewable energy that is subject to evaluation in LR1-3 2) Adoption of renewable energy power menus with additionality other than 1) above. 3) Other procurement of non-fossil energy for use in energy storage facilities on the building side.
- | - |  |  | Level 2 | (No corresponding level)
3 | 3 |  |  | Level 3 | No countermeasures
4 | 4 |  |  | Level 4 | Facilities, such as energy storage, are being introduced to expand the introduction of non-fossil energy such as the use of renewable energy (tangible) from any effort of *1
5 | 5 |  |  | Level 5 | In addition to Level 4, operational initiatives are being made to expand the introduction of non-fossil energy (intangible) from any effort of *2
0 | 0 |  |  | Outline of env. efforts
*1: Level 4; Introduction of energy storage facilities to promote the use of renewable energy (tangible)
1) Energy storage equipment: electric batteries, etc.
2) Heat storage equipment: heat storage [heat, heat, hot water], etc.
3) Others: Hydrogen storage derived from renewable energy electricity, etc., which are effective in the use of renewable energy (e.g., electrification of combustion equipment in factory production facilities)
*2: Level 5; Operational initiatives to promote the use of renewable energy (intangible).
- Mainly by measures for operation using energy storage equipment.
|  | 4.4 | Promoting Commissioning
[7 empty] | Weighting coef.(default) = | 0.1
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct
- | - |  |  | Level 1 | (No corresponding level)
- | - |  |  | Level 2 | (No corresponding level)
3 | 3 |  |  | Level 3 | No countermeasures
4 | 4 |  |  | Level 4 | Efforts from [1] are introduced.
5 | 5 |  |  | Level 5 | In addition to Level 4, more than 2 efforts from [2] are introduced.
0 | 0 |  |  | Outline of env. efforts
Efforts to be evaluated
[5 empty] | 3 | Description
|  |  |  | No.1 | Yes | [1] | 1) Clarify the Client Requirements (OPR) and update them as needed.
|  |  |  | No.2 |  |  | 2) Strive to form a consensus among the parties involved such as the client, designer, and constructor, and prepare a record document describing the history and results.
|  |  |  | No.3 |  | [2] | 3) Review whether the design and construction documents are corresponding to the OPR.
|  |  |  | No.4 | Yes |  | 4) Evaluate VE and CD in construction phase to determine whether they are suitable for realizing OPR.
|  |  |  | No.5 |  |  | 5) Plan to conduct functional performance tests immediately after completion.
|  |  |  | Total | 1 | items
Note on F21: 住宅部分と非住宅部分の床面積による加重平均（小数第2位で切捨）

## ENcalc
n LR1 Data transcription from "Building Energy Consumption Performance Assurance Plan" etc. | [11 empty] | ■Building Name | XXX Building |  | n
1 | Matters concerning the prevention of heat loss through exterior walls, windows, etc. | [14 empty] | 4 |  | -14.2857 | 16.8571 | 4 |  | -25 | 27.25
|  | Other than Apt. |  | [BPI][BPIm] = | 0.97 |  | Zone 3 |  | Zone 1-7 | 3 |  |  |  |  | Not applicable | レベル | 1～7地域 | a（傾き） | ｂ（切片） | レベル | Zone 8 | a（傾き） | ｂ（切片）
[9 empty] | Zone 8 | 3 |  |  |  |  | Less than Grade 3 | 1 | 1.03 | 0 | 1 | 1 | 1.03 | 0 | 1
[15 empty] | Grade 3 | 2 | 1 | -33.3333 | 35.3333 | 2 | 1 | -33.3333 | 35.3333
|  | Apt. | Housing Performance Indication Standard |  | Not applicable |  | equivalent * | [7 empty] | Grade 4 | 3 | 0.97 | -33.3333 | 35.3333 | 3 | 0.97 | -33.3333 | 35.3333
|  | * | If multiple grades are mixed, evaluate based on the lowest grade. | [11 empty] | Grade 5 | 4 | 0.9 | -14.2857 | 16.8571 | 4 | 0.93 | -25 | 27.25
|  |  |  | Floor area [㎡] | Floor area ratio | [9 empty] | Grade 6 or above | 5 | 0.8 | -10 | 13 | 5 | 0.85 | -12.5 | 15.625
|  |  | Other than Apt. | 7000 | 1 |  | 3 | [7 empty] | No Grade input
|  |  | Apt. | 0 | 0 |  | 1 | [7 empty] | No BPI input
| LR1/1. Control of Heat Load on Building Envelopes |  |  |  | 3
2 | Primary energy consumption performance | [13 empty] | BEI* | 4 |  | -4 | 6 | 住宅
| n | Transcription of BEI and other indicators | [12 empty] | BEI | 5 |  | 0 | 0 | 5 |  | 0 | 0
|  |  |  | Other than Apt. | Apt. ** |  |  |  |  | Other than Apt. | Apt. |  |  |  |  | レベル | 評価建物 | a（傾き） | ｂ（切片） | レベル | 評価建物 | a（傾き） | ｂ（切片）
|  |  | [BEI＊] [BEIm＊] = | 0.5 |  |  | Prim. Ene. Cons. performance w/o renewables |  |  | 4 | 0 |  |  |  |  | 1 | 0.9 | -10 | 10 | 1 | 1.1 | -10 | 12
|  |  | [BEI] [BEIm] = | 0.25 |  |  | Prim. Ene. Cons. Perf. incl. on-site renewables (total) |  |  | 5 | 0 |  |  |  |  | 2 | 0.8 | -5 | 6 | 2 | 1 | -10 | 12
|  |  | [BEI+]= |  |  |  | Prim. Ene. Cons. Perf. incl. on-site and off-site renewables |  |  | 0 | ― |  |  |  |  | 3 | 0.6 | -10 | 9 | 3 | 0.9 | -10 | 12
[7 empty] | ** For apartments, enter the “primary energy consumption reduction rate” including common areas converted to BEI or BEI＊ (1 - “primary energy consumption reduction rate”). Evaluations are also acceptable with BEI and BEI＊ for dwelling areas only (common areas may be omitted). | [8 empty] | 4 | 0.5 | -4 | 6 | 4 | 0.8 | -3.3333 | 6.6667
|  | Conditions for building types other than Apt. | [11 empty] | Yes |  | 5 | 0.25 |  |  | 5 | 0.5
|  |  |  | Evaluated level 4 or higher with BEI+ |  |  | Applicable if the on-site renewable energy is introduced, and the effectiveness is presented, and [BEI＊] ≤ 0.5. | [13 empty] | 0.7 | -10 | 12
|  |  |  | Overview of eligible off-site renewable energy | 〇〇kW installed in 〇〇 City, used 〇〇GJ/yr, etc. |  |  |  | ←Fill in the details of [1] and [2] below.
For BEI+, it is necessary to confirm the effectiveness of off-site renewable energy, and the following points should be presented. [1] Presentation of an overview of the evaluated “renewable energy power generation equipment/facilities” (location, capacity, specifications, etc.) [2] Presentation of annual energy usage review materials (supply and demand balance review materials) [3] Some kind of renewable energy facilities should be planned to be installed on site (Not applicable where there are no renewable energy facilities on site).
Conditions for Apt.
|  |  |  | Evaluated level 4 or higher with BEI＊ |  |  | Applicable only for buildings of more than 6 floors or when effect of introducing renewable energy is low due to reasons such as shade.
|  |  |  | Reasons why effect of introduction is low | [9 empty] | No (Evaluation based on Calculation Program)
|  |  |  | Evaluated based on specification std. |  |  |  |  | BEI＊＝ | 0.8 | equivalent |  |  | 1
|  |  |  | Floor area evaluated based on specification std. |  |  | ㎡ |  | ←No input of floor area [㎡] to be evaluated. |  |  |  |  | 2
|  |  |  | Floor area evaluated based on | 0 |  | ㎡ | 0 | [5 empty] | 4
|  |  |  | Level 2 (meeting "Standards for the prevention of heat loss through the exterior walls and windows of residential parts and standards for primary energy consumption" (MLIT Notification No. 266, revised in November 4, 2022). hereinafter referred to as the "Specification Standards")) and Level 4 (meeting "Certification Standards for the exterior walls and windows of residential parts and Certification Standards for Primary Energy Consumption" (MLIT Notification No. 1106, November 4, 2022. Hereinafter referred to as "Certification Specification Standards"). If the above levels are not met, select Level 1. | [9 empty] | ←No input of floor area [㎡] to be evaluated.
[7 empty] | Other than Apt. | Apt.
| LR1/3. Efficiency in Building Service System | [5 empty] | 5 | 0 | [5 empty] | ERROR (There is an error in the input.)
<運用期間が1年未満の場合>
期間積算の基準一次エネルギー消費量に対する設計一次エネルギー消費量の比率 [BEITC] を[BEI]欄に入力
| n | Input of Area subject to evaluation by Building type and BEI/BEIm settings, etc.
|  |  |  | Floor area [㎡] | Floor area ratio |  | Level 1 | Level 2 | Level 3 | Level 4 | Level 5
|  | Bldg. type [1] | Off, Sch | 7000 | 1 |  | 0.9 | 0.8 | 0.6 | 0.5 | 0.25
|  | Bldg. type [2] | Rtl, Htl | 0 | 0 |  | 0.9 | 0.8 | 0.7 | 0.5 | 0.25
|  | Bldg. type [3] | Rst, Hal, Hsp | 0 | 0 |  | 0.9 | 0.85 | 0.7 | 0.5 | 0.25
|  | Bldg. type [4] | Fct | 0 | 0 |  | 0.9 | 0.75 | 0.6 | 0.5 | 0.25
|  | Bldg. type [6] | Other than Apt | 7000 |  |  | 0.9 | 0.8 | 0.6 | 0.5 | 0.25
|  | Bldg. type [5] | Apt | 0 |  |  | 1.1 | 1 | 0.9 | 0.8 | 0.5
3 | Transcription of Primary energy consumption of the building, etc. (for WLC calculation)
Select the following if you do not use the calculation program for apartments (dwelling area).
|  | Heating | [5 empty] | Cooling | [5 empty] | A | a
|  |  | A: Method in which the entire dwelling unit is heated | [5 empty] | a: Method in which the entire dwelling unit is cooled |  |  |  |  | B | b
|  |  | B: Method in which only the living space is heated (Continuous heating) | [5 empty] | b: Method in which only the living space is cooled (Intermittent cooling) |  |  |  |  | C | －
|  |  | C: Method in which only the living space is heated (Intermittent heating) | [5 empty] | －: Other than above (or unknown) |  |  |  |  | －
－: Other than above (or unknown)
| n | Corridor type in common areas | [5 empty] | outdoor corridor | 522 | MJ/yr-㎡
[8 empty] | indoor corridor | 801 | MJ/yr-㎡
| n | Result of the calculation program for apartment | [5 empty] | * can be omitted. Guestrooms may be included in dwelling unit subtotal.
|  | Primary energy consumption |  |  |  |  | [MJ/yr] | Dwelling unit subtotal | Common area* | Guestrooms in common area* as dwelling unit | Total
|  | Floor area [㎡] to be evaluated by calculation program | [8 empty] | 0 | ㎡ |  |  | 6000 | 600
|  | A. Standard primary energy consumption | [8 empty] | 0 |  |  |  | 4032000 | 480000
|  | B. Design primary energy consumption (subtotal including CGS effect） | [8 empty] | 0 |  | excl. PV |  | 2950000 | 432000
|  | C. Deduction related to CGS-generated electricity sales (enter negative value) | [8 empty] | 0 |  |  |  | 0
|  | D. Primary energy consumption of other equipment, such as home appliances | [8 empty] | 0 |  |  |  | 1062000 | 0
|  | E. Electric power generated (by CGS) | [8 empty] | 0 |  |  |  | 0
|  | F. Electric power generated (by PV) | [8 empty] | 0 |  | incl. electricity sales |  | 58900 | 0
|  | G. Design primary energy consumption (subtotal including CGS & PV effect） | [8 empty] | 0 |  | incl. PV (in-house cons.) |  | 2891100 | 0
[7 empty] | <Ref.> BEI＊ | - | - | - | - |  | excl. PV
|  | Note; |  |  |  |  | BEI | - | - |  | - |  | incl. PV (total generation)
- "A" and "B" include primary energy of other equipment "D."
- "B" does not take into account reductions achieved through renewable energy "F". "G" takes into account "F" (in-house consumption).
- Electricity sold to others through Feed-in-Tariffs is excluded from the assessment.
For apartments, input the primary energy consumption, as this is necessary for calculating GHG emissions at operation stage. For buildings other than apartment, inputting primary energy consumption isn't needed since BEIs are used for GHG calculation at operation stage and for scoring "LR1/3. Efficiency in Building Service System."
Primary energy consumption (standard calculation) used for calculating GHG at operation stage
[2] Building-related Initiatives | [12 empty] | GJ/yr
| Other than Apt. |  | BEI＊= | 0.5 | [6 empty] | Eval. bldg. |  | Ref. bldg. | No BEI input
[11 empty] | 5425 |  | 10850
[5 empty] | Floor area |  | Prim. Energy |  | GHG conversion coefficient
[5 empty] | ㎡ |  | Statistic data [MJ/yr-㎡] |  | kg-CO2eq/MJ |  |  |  |  | 電気％ | 0.78
|  | Office | Office |  | 7000 |  | 1550 |  | #VALUE! |  |  |  |  | 78%
|  |  | Government buildings |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 77%
|  |  | Research institutes |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 63%
|  | School | Kindergartens/ nursery schools |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 70%
|  |  | ES/JHS | Hokkaido | 0 |  | 0 |  | #VALUE! |  |  |  |  | 67%
|  |  |  | Other area | 0 |  | 0 |  | #VALUE! |  |  |  |  | 74%
|  |  | High schools |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 74%
|  |  | Universities/ colleges |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 66%
|  | Retailers | Department, supermarkets |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 73%
|  |  | Convenience store |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 100%
|  |  | Electronics retailers, |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 71%
|  |  | Other stores |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 89%
|  | Restaurants |  |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 51%
|  | Halls | Theatres/halls |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 73%
|  |  | Exhibition facilities |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 77%
|  |  | Sports facilities |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 69%
|  | Factories |  |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 100%
|  | Hospitals |  |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 48%
|  | Hotels |  |  | 0 |  | 0 |  | #VALUE! |  |  |  |  | 42%
|  | Non Apt. | Subtotal |  | 7000 |  | 10850 | GJ/yr | #VALUE! |  |  |  |  | 電気分 | 8463
|  | ■自然エネルギーの直接利用量 |  |  | 用途別面積
|  |  | LR1/2. 自然ｴﾈﾙｷﾞｰ利用 |  | ㎡ |  | ﾚﾍﾞﾙ３ | ﾚﾍﾞﾙ４ | ﾚﾍﾞﾙ５ | 採点結果 | 削減量
|  |  |  | 小中高校・集合住宅 | 0 |  |  |  |  | 3 | 0
|  |  |  | 上記以外 | 7000 |  |  |  |  | 3 | 0 | MJ/年㎡
| n | Initiatives for Efficient Operation |  |  |  |  | Level 3 | Level 4 | Level 5 | Score weighted average | Reduction
[5 empty] | 4.1 Monitoring, 4.2 Operation & Management System |  | 1 | 0.975 | 0.95 | 3 | 1
GJ/yr
| Apt. | [9 empty] | Eval. bldg. |  | Ref. bldg.
|  | Dwelling area (including guest rooms) | [5 empty] | Eval. bldg. | Ref. bldg. |  | 0 |  | 0
|  |  |  | Evaluation based on Calculation Program | 0 | ㎡ |  | 0 | 0 | GJ/yr |  |  |  | No Prim. Ene. input
|  |  |  | Evaluation not based on Calculation Program | 0 | ㎡ |  | 1214.049 | 883.5276 | MJ/yr-㎡
|  | Common area |  | BEI＊= | -
[5 empty] | 0 | ㎡ |  | #VALUE! | 801 | MJ/yr-㎡ | 0 |  | 0 | No corridor input
[3] Above Initiatives + Other On-site Measures
| Other than Apt. |  |  | BEI = | 0.25 | [5 empty] | 2712.5 |  |  | →レベル４以上はBEIにPV売電分含む
| Apt. |  | Dwelling area |  |  |  | On-site measures | 0 | GJ/yr |  | 0 |  |  | →PV・コジェネ売電分含む
|  |  | Common area | BEI = | -
[5 empty] | 0 | ㎡ |  | #VALUE! | 801 | MJ/yr-㎡ | 0 |  |  | →PV売電分含む
<Ref.>[4] Above Initiatives + Other Off-site Measures
| Other than Apt. |  |  | BEI+ = | 0.25 | [5 empty] | 2712.5
Note on G21: 入力するＢＥＩ（オンサイトの再生可能エネルギーを含む）は、レベル３未満の場合は自己消費分で評価する。レベル３以上の場合は総量（売電分含む）で評価してよい。
Note on H117: Enter the BEI* (dwelling area, common area, or entire building) used to calculate the primary energy consumption of common areas
Note on H124: Enter the BEI (dwelling area, common area, or entire building) used to calculate the primary energy consumption of common areas

## LR2
[11 empty] | n Building Name | XXX Building
|  |  |  | 1 | Level 1 | ■Level 1
|  |  |  | 2 | Level 2 | ■Level 2 |  |  | プルダウン選択肢 | <N.A.> | Yes | Not apply | Preliminary design stage
|  |  |  | 3 | Level 3 | ■Level 3 | [5 empty] | Apply | Execution design stage
|  |  |  | 4 | Level 4 | ■Level 4 | [6 empty] | Construction completion stage
|  |  |  | 5 | Level 5 | ■Level 5 |  |  |  |  | Yes
|  |  |  | 0 | Level | Level |  |  |  |  | No
|  | LR2 Resources & Materials | [5 empty] | Select from pull-down menus or enter figures and comments. |  |  |  |  | Execution design stage
The outline of efforts for environment should be filled in short if the score exceeds Level 3. If there is a lot to write, describe it on the consideration sheet.
|  | 1 | Water Resources
|  | 1.1 | Water Saving
[7 empty] | Weighting coef.(default) = | 0.4
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
1 |  |  |  | Level 1 | No systems for saving water.
- |  |  |  | Level 2 | (No corresponding level)
3 |  |  |  | ■Level 3 | Major faucets are equipped with water-saving valve.
4 |  |  |  | Level 4 | In addition to water-saving valve, other water-saving equipment (such as flush-mimicking sound systems, water-saving toilets) is used.
- |  |  |  | Level 5 | (No corresponding level)
0 |  |  |  | Outline of env. efforts |  |  |  |  | Note; Describe introduced technics.
|  | 1.2 | Rain Water & Waste Water Use
|  |  |  | 1.2.1 Rain Water Use System |  |  |  |  | 1.2.2 Waste Water Reuse System
1.2.1 | 1.2.2 | [5 empty] | Weighting coef.(default) = | 0.7 |  |  |  | Weighting coef.(default) = | 0.3
小中高は既存も新築の基準 |  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct
- | - |  |  | Level 1 | (No corresponding level) |  |  |  | Level 1 | (No corresponding level)
- | - |  |  | Level 2 | (No corresponding level) |  |  |  | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | No systems for using rain water. |  |  |  | ■Level 3 | No systems for reusing waste water.
4 | 4 |  |  | Level 4 | Rain water is used. |  |  |  | Level 4 | Waste water is reused.
5 | 5 |  |  | Level 5 | Rain water usage rate ≦ 20%. |  |  |  | Level 5 | More than two types of waste water are used
0 | 0 |  |  | Outline of env. efforts |  |  |  |  | Outline of env. efforts
|  |  |  | Rain water usage rate |  |  |  |  | Type of wastewater | Adopted | Type |  | Location
[5 empty] | = | Rain water use [m3] |  |  | No.1 | - | Wastewater
[8 empty] | Potable water use [m3] + Rain water use [m3] + Waste water use [m3] | No.2 |  | Not recycling rainwater
[9 empty] | No.3 |  | Recycling rainwater |  | On-site (in the block)
[9 empty] | No.4 |  | Recycling rainwater |  | Public Infrastructure (off the block)
[9 empty] | No.5 |  | Sewage
[9 empty] | No.6 | - | Industrial water
[9 empty] | No.7 |  | Reclaimed water, grey water |  | Public Infrastructure (off the block)
[9 empty] | No.8 |  | Other type than reclaimed water and grey water
|  | 2 | Reducing Use of Non-renewable Resources
|  | 2.1 | Reducing Use of Materials
| Sch校版基準 | [5 empty] | Weighting coef.(default) = | 0.1
Min | 0 |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  |  |  | Remarks |  | 0 | Sch
0 | - |  |  | Level 1 | (No corresponding level) |  |  |  | Buildings with wood as the main structural component are excluded from this assessment. |  | Level 1
0 | - |  |  | Level 2 | Major structural elements are made of non-wood materials (RC/SRC/S), and earned 0 points in total for the table of the efforts to be evaluated. | [5 empty] | Level 2
1 | 3 |  |  | ■Level 3 | Major structural elements are made of non-wood materials (RC/SRC/S), and earned 1-2 points in total for the table of the efforts to be evaluated. | [5 empty] | Level 3
3 | - |  |  | Level 4 | Major structural elements are made of non-wood materials (RC/SRC/S), and earned 3-4 points in total for the table of the efforts to be evaluated. | [5 empty] | Level 4
5 | 5 |  |  | Level 5 | Major structural elements are made of non-wood materials (RC/SRC/S), and earned 5 points or more in total for the table of the efforts to be evaluated. | [5 empty] | Level 5
| 0 |  |  | Outline of env. efforts
Efforts to be evaluated
[5 empty] | 3 | Assessment Item |  |  | Description |  |  |  | Point allocation
Max | [5 empty] | Buildings with wood as the main structural component
4 |  |  |  | No.1 | 1 | 1) Concrete strength FC and main rebar strength F of main structure [unit: N/mm2] |  |  | More than Fc = 36, and less than F = 390 (1 point) More than Fc = 60, and less than F = 490 (3 points) More than Fc = 100, and less than F = 590 (4 points) |  |  |  | 1～4
4 |  |  |  | No.2 | 1 | 2) Steel frame strength F in main structure frame [unit: N/mm2] |  |  | F = 325 or more but less than 355 (1 point) F = 355 or more but less than 440 (3 points) F = 440 or more (4 points) |  |  |  | 1～4
4 |  |  |  | No.3 |  | 3) Other measures related to major structural elements |  |  | Use of pre-stressed concrete (which reduces material cross section, thereby reducing materials used). (1 point) Equivalent measures. (1 point each) |  |  |  | 1～
|  |  |  | Total | 2 | points | [6 empty] | 12
|  | 2.2 | Continuing Use of Existing Structural Frame, etc.
[7 empty] | Weighting coef.(default) = | 0.2
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
- |  |  |  | Level 1 | (No corresponding level)
- |  |  |  | Level 2 | (No corresponding level)
3 |  |  |  | ■Level 3 | The existing building frame is not reused.
- |  |  |  | Level 4 | (No corresponding level)
5 |  |  |  | Level 5 | Existing building frame is reused.
0 |  |  |  | Outline of env. efforts
|  | 2.3 | Use of Recycled Materials as Structural Materials
[7 empty] | Weighting coef.(default) = | 0.2
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
- | 1 |  |  | Level 1 | (No corresponding level)
- | 2 |  |  | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | No recycled materials are used in the main parts for structural strength.
- | 4 |  |  | Level 4 | (No corresponding level)
5 | 5 |  |  | Level 5 | Recycled materials are used in the main parts for structural strength.
0 | 0 |  |  | Outline of env. efforts |  |  |  |  | Note; State introduced materials and its application.
|  |  |  | Materials | Type of materials |  | Type of recognition
|  |  |  | No.1 | aggregate |  |  | Not introduced | No. | Type of recognition
|  |  |  | No.2 | cement |  |  | Not introduced | 0 | Not introduced
|  |  |  | No.3 | Recycled steel |  |  | Not introduced | 1 | Designated green procurement items
|  |  |  | No.4 | Lumber |  |  | Not introduced | 2 | Eco Mark products
|  |  |  | No.5 | Other |  |  | Not introduced | 3 | Specific items designated by local governments, etc.
|  | 2.4 | Use of Recycled Materials as Non-structural Materials
[7 empty] | Weighting coef.(default) = | 0.2
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
1 | 1 |  |  | Level 1 | No recycled materials are used.
- | 2 |  |  | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | One type of recycled material is used.
4 | 4 |  |  | Level 4 | Two types of recycled material are used.
5 | 5 |  |  | Level 5 | Three or more types of recycled material are used.
0 | 0 |  |  | Outline of env. efforts |  |  |  |  | Note; State introduced materials and its application.
|  |  |  | Materials | Type of recognition |  | Material name
Designated green procurement items
Eco Mark products
Specific items designated by local governments, etc.
|  | 2.5 | Timber from Sustainable Forestry
[7 empty] | Weighting coef.(default) = | 0.1
小中高は既存も新築の基準 |  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt | [6 empty] | Remarks
- | 1 |  |  | Level 1 | (No corresponding level) | [6 empty] | Inapplicable (N.A.) if no timber is used.
2 | 2 |  |  | Level 2 | Timber from sustainably managed forests is not used.
3 | 3 |  |  | ■Level 3 | Timber from sustainably managed forests supplied less than 10% of timber usage, or no timber is used, even in the structural skeleton.
4 | 4 |  |  | Level 4 | Timber from sustainably managed forests supplies 10-50% of timber usage.
5 | 5 |  |  | Level 5 | Timber from sustainably managed forests supplies 50% or more of timber usage.
0 | 0 |  |  | Outline of env. efforts
|  |  |  | Proportion of timber used |  | ＝ | Total quantity of timber used from sustainable forests (volume) [m3]
Total quantity of timber used in the building (volume) [m3]
|  | 2.6 | Reusability of Components and Materials
[7 empty] | Weighting coef.(default) = | 0.2
Min |  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
0 |  |  |  | Level 1 | (No corresponding level)
0 |  |  |  | Level 2 | (No corresponding level)
0 |  |  |  | ■Level 3 | 0 point in total from the table of the efforts to be evaluated, which are taken as efforts to promote material recycling on demolition.
1 |  |  |  | Level 4 | 1 point in total from the table of the efforts to be evaluated, which are taken as efforts to promote material recycling on demolition.
2 |  |  |  | Level 5 | 2 points or more in total from the table of the efforts to be evaluated, which are taken as efforts to promote material recycling on demolition.
|  |  |  | Outline of env. efforts |  |  |  |  | Note; Describe the extent of efforts in terms of countermeasure area ratio, etc.
Efforts to be evaluated
[5 empty] | 3 | Description
|  |  |  | No.1 |  | 1) The structure of finishing materials can be separated easily.
|  |  |  | No.2 |  | 2) Interior finishes and equipment are not entangled, and each can easily be removed separately for demolition, refurbishment and remodeling.
|  |  |  | No.3 |  | 3) Reusable unit materials are used.
|  |  |  | No.4 |  | 4) Structural materials or their units can easily be disassembled and reused.
|  |  |  | Total | 0 | items
|  |  |  | 2.6.1 躯体のリサイクル・リユース |  |  |  | <N.A.> | 2.6.2 屋根材のリサイクル・リユース |  |  |  | <N.A.>
[7 empty] | Weighting coef.(default) = | 0 |  |  |  | Weighting coef.(default) = | 0
短期使用 | 短期使用 |  |  | 5 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  |  |  | 4 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
1 | 1 |  |  | Level 1 | 躯体材料が着脱しやすいように設計されているなど、躯体材料のリサイクル・リユースについて取組無し |  |  |  | Level 1 | 屋根材・下地材が着脱しやすいように設計されているなど、屋根材・下地材のリサイクル・リユースについて取組無し
2 | 2 |  |  | Level 2 | 躯体材料の一部が着脱でき、それらをリサイクルもしくはリユースできる |  |  |  | Level 2 | 屋根材・下地材の一部が着脱でき、それらをリサイクルもしくはリユースできる
3 | 3 |  |  | Level 3 | 躯体材料の大半が着脱できるか、もしくは、単種類の材料で構成されていて、それらを少なくともリサイクルはできる |  |  |  | Level 3 | 屋根材・下地材の大半が着脱できるか、もしくは、単種類の材料で構成されていて、それらを少なくともリサイクルはできる
4 | 4 |  |  | Level 4 | レベル3に加えて、躯体材料の一部は規格材で構成されていてリユースできる |  |  |  | ■Level 4 | レベル3に加えて、屋根材の一部は規格材で構成されていてリユースできる
5 | 5 |  |  | ■Level 5 | レベル3に加えて、躯体材料の大半は規格材で構成されていてリユースできる |  |  |  | Level 5 | レベル3に加えて、屋根材の大半は規格材で構成されていてリユースできる
0 | 0
|  |  |  | 2.6.3 外壁材のリサイクル・リユース |  |  |  | <N.A.> | 2.6.4 内装材のリサイクル・リユース |  |  |  | <N.A.>
[7 empty] | Weighting coef.(default) = | 0 |  |  |  | Weighting coef.(default) = | 0
短期使用 | 短期使用 |  |  | 4 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  |  |  | 4 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
1 | 1 |  |  | Level 1 | 外壁材・下地材が着脱しやすいように設計されているなど、外壁材・下地材のリサイクル・リユースについて取組無し |  |  |  | Level 1 | 内装材・下地材が着脱しやすいように設計されているなど、内装材・下地材のリサイクル・リユースについて取組無し
2 | 2 |  |  | Level 2 | 外壁材・下地材の一部が着脱でき、それらをリサイクルもしくはリユースできる |  |  |  | Level 2 | 内装材・下地材の一部が着脱でき、それらをリサイクルもしくはリユースできる
3 | 3 |  |  | Level 3 | 外壁材・下地材の大半が着脱できるか、もしくは、単種類の材料で構成されていて、それらを少なくともリサイクルはできる |  |  |  | Level 3 | 内装材・下地材の大半が着脱できるか、もしくは、単種類の材料で構成されていて、それらを少なくともリサイクルはできる
4 | 4 |  |  | ■Level 4 | レベル3に加えて、外壁材の一部は規格材で構成されていてリユースできる |  |  |  | ■Level 4 | レベル3に加えて、内装材の一部は規格材で構成されていてリユースできる
5 | 5 |  |  | Level 5 | レベル3に加えて、外壁材の大半は規格材で構成されていてリユースできる |  |  |  | Level 5 | レベル3に加えて、内装材の大半は規格材で構成されていてリユースできる
0 | 0
|  |  |  | 2.6.5 設備機器のリサイクル・リユース |  |  |  | <N.A.> | 2.6.6 外構資材のリユース |  |  |  | <N.A.>
[7 empty] | Weighting coef.(default) = | 0 |  |  |  | Weighting coef.(default) = | 0
短期使用 | 短期使用 |  |  | 1 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt |  |  |  | 1 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
1 | 1 |  |  | ■Level 1 | 評価する取組みがない。 |  |  |  | ■Level 1 | 評価する取組みがない。
2 | - |  |  | Level 2 | 評価する取組みが1つ。 |  |  |  | Level 2 | (該当するレベルなし)
3 | 3 |  |  | Level 3 | 評価する取組みが2つ。 |  |  |  | Level 3 | 評価する取組みが1つ。
4 | 4 |  |  | Level 4 | 評価する取組みが3つ。 |  |  |  | Level 4 | 評価する取組みが2つ。
5 | 5 |  |  | Level 5 | 評価する取組みが4つ以上。 |  |  |  | Level 5 | 評価する取組みが3つ以上。
0 | 0 |  |  | 0 | ← 直接入力 | しない |  |  | 0 | ← 直接入力 | しない
|  |  |  | 評価する取組み |  |  |  |  | 評価する取組み
|  |  |  | 採用項目 | 取組み |  |  |  | 採用項目 | 取組み
|  |  |  | ○ | 1)使用材料種類の集約 |  |  |  | ○ | 1)外構に植栽する樹木の移設・再使用を前提とした植栽方法の採用
|  |  |  | ○ | 2)配管材の規格一律化・規格材の活用 |  |  |  |  | 2）屋根緑化や壁面緑化等の建Rtl緑化に用いる植Rtlの移設・再使用を前提とした植栽方法の採用
|  |  |  | ○ | 3)設備機器（空調機）の規格化 |  |  |  | ○ | 3）舗装用平板やブロック等道路用材について、移設・再使用を前提とした資材・Fct法の採用
|  |  |  | ○ | 4)設備機器（照明）の規格化 |  |  |  | ○ | 4）擁壁や植栽ブロック等土木用材について、移設・再使用を前提とした資材・Fct法の採用
[5 empty] | 5)設備機器の着脱性の確保 |  |  |  |  | 5)その他（記述）
6)設備機器と内装材・外装材・屋根材との錯綜を回避した納まり
[5 empty] | 7)修理・部品交換しやすい設備機器の使用 |  |  |  | 取組数 | 0
8)その他（記述）
|  |  |  | 取組数 | 0
|  | 2.7 | 廃棄Rtl発生量の最小化 |  |  |  |  | <N.A.>
[7 empty] | Weighting coef.(default) = | 0
短期使用 |  |  |  | 2 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
1 | 1 |  |  | Level 1 | (該当するレベルなし)
2 | 2 |  |  | ■Level 2 | 評価する取組みがない。
3 | 3 |  |  | Level 3 | 評価する取組みが1つ。
4 | 4 |  |  | Level 4 | 評価する取組みが2つ。
5 | 5 |  |  | Level 5 | 評価する取組みが3つ以上。
0 | 0 |  |  | 0 | ← 直接入力 | しない
評価する取組み
[5 empty] | 採用項目 | 取組み
[5 empty] | ○ | 自然素材利用による建築構造体の軽量化
[5 empty] | ○ | 施Fct廃棄Rtl減量計画・マネジメント手法の整備
リース・レンタル材料及び設備の採用
リユース＆リサイクルルートと受け入れ先確保（リース・レンタルは除く）
[5 empty] | ○ | その他（記述）
[5 empty] | 取組数 | 0
|  | 3 | Avoiding the Use of Materials with Pollutant Content
|  | 3.1 | Use of Materials without Harmful Substances
[7 empty] | Weighting coef.(default) = | 0.3
Min |  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
0 |  |  |  | Level 1 | (No corresponding level)
0 |  |  |  | Level 2 | (No corresponding level)
0 |  |  |  | ■Level 3 | There are no building materials to be confirmed to contain no substances specified in the Pollutant Release and Transfer Register Law. Or the inspection has not been carried out.
1 |  |  |  | Level 4 | There are 1-3 building materials to be confirmed to contain no substances specified in the Pollutant Release and Transfer Register Law.
4 |  |  |  | Level 5 | There are 4 or more building materials to be confirmed to contain no substances specified in the Pollutant Release and Transfer Register Law.
|  |  |  | Outline of env. efforts |  |  |  |  | Note; State the types of building materials that have been confirmed.
Types of materials to be confirmed to contain no specified substances
[5 empty] | 3 | Category | Type of materials |  |  | Specified substances | Category | Type of materials
[6 empty] | Adhesives | For vinyl tile floors and seating |  |  |  | Paints | For fittings (wooden and metal)
Non (Confirmed) | [6 empty] | For tile |  |  |  |  | For wooden parts (frames for floor and ceiling)
[7 empty] | For wallpaper |  |  |  |  | For structural materials
[7 empty] | For floor board |  |  |  |  | For walls
[6 empty] | Sealants | For sash |  |  |  | Anti-corrosion treatment | For frames
[7 empty] | For glass |  |  |  |  | For materials other than frames
[7 empty] | For tile joint |  |  |  | Undercoats | For materials for coated floors
[7 empty] | For wall joint |  |  |  | Floor coverings | For finishing wax
[6 empty] | Waterproofing materials | Primer for waterproofing |  |  |  | Preservatives | For wooden parts
[7 empty] | For paint (surface coating) |  | Total | 0 | types
|  | 3.2 | Avoidance of CFCs and Halons
3.2.1 Fire Retardant
[7 empty] | Weighting coef.(default) = | 0.33333
|  |  |  | 2 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt | [6 empty] | Remarks
1 |  |  |  | Level 1 | Halon flame retardants with high ODP/GWP are used (incl. critical uses). | [6 empty] | Excluded from the assessment; buildings with no fire-extinguishing equipment, or sprinklers only, or no gas fire extinguishing facilities. Exclude foam extinguisher.
2 |  |  |  | ■Level 2 | Halogenated flame retardants are used.
- |  |  |  | Level 3 | (No corresponding level)
4 |  |  |  | Level 4 | Inert gas flame retardants are used. Or, flame retardants with 0 ODP and less than 50 GWP are used.
- |  |  |  | Level 5 | (No corresponding level)
0 |  |  |  | Outline of env. efforts |  |  |  |  | Note; Describe the type of fire extinguishing agent, etc.
|  |  |  | ODP |  | GWP
3.2.2 Foaming Agents (Insulation Materials, etc.)
[7 empty] | Weighting coef.(default) = | 0.33333
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
1 |  |  |  | Level 1 | Not adequate for Level 3
- |  |  |  | Level 2 | (No corresponding level)
3 |  |  |  | ■Level 3 | Insulation foaming materials with zero-ODP are used.
4 |  |  |  | Level 4 | Insulation foaming materials with zero-ODP and low GWP (less than 10 in 100-year value) are used.
5 |  |  |  | Level 5 | Insulation foaming materials with zero-ODP and low GWP (less than 1 in 100-year value) are used; or, no insulation foaming material used.
0 |  |  |  | Outline of env. efforts |  |  |  |  | Note; If no foaming agent is used, state it here.
|  |  |  | ODP |  | GWP
3.2.3 Refrigerants
[7 empty] | Weighting coef.(default) = | 0.33333
|  |  |  | 4 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt | [6 empty] | Remarks
- |  |  |  | Level 1 | (No corresponding level) | [6 empty] | Exclude from assessment if no refrigerant gases are used.
2 |  |  |  | Level 2 | HCFC is used as the refrigerant.
3 |  |  |  | Level 3 | Refrigerant of ODP = 0 is used as the refrigerant.
4 |  |  |  | ■Level 4 | Natural refrigerants and new chilling systems (ODP = 0) with GWP less than 50 are used.
- |  |  |  | Level 5 | (No corresponding level)
0 |  |  |  | Outline of env. efforts |  |  |  |  | Note; Describe refrigerant type, etc.
|  |  |  | ODP |  | GWP

## LR3
[11 empty] | n Building Name | XXX Building
プルダウン選択肢 |  |  |  | 1 | Level 1 | ■Level 1
|  |  |  | 2 | Level 2 | ■Level 2 |  |  | プルダウン選択肢 | <N.A.> | Yes | Not apply | Preliminary design stage
|  |  |  | 3 | Level 3 | ■Level 3 | [5 empty] | Apply | Execution design stage
|  |  |  | 4 | Level 4 | ■Level 4 | [6 empty] | Construction completion stage
|  |  |  | 5 | Level 5 | ■Level 5 |  |  |  |  | Yes
|  |  |  | 0 | Level | Level |  |  |  |  | No
|  | LR3 Off-site Environment | [5 empty] | Select from pull-down menus or enter figures and comments. |  |  |  |  | Execution design stage
The outline of efforts for environment should be filled in short if the score exceeds Level 3. If there is a lot to write, describe it on the consideration sheet.
|  | 1 | Consideration of Global Warming |  |  |  |  | #VALUE! | [7 empty] | 非住宅 |  |  |  | 住宅
[6 empty] | Weighting coef.(default) = |  | 0.33333 | [5 empty] | 2024年版 |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! |  | #VALUE! | #VALUE!
|  |  |  | #VALUE! | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct |  |  | 7000 | Apt |  | 0 | Remarks |  | 大規模 | 小規模 | レベル | 基準値 | a（傾き） | ｂ（切片） | レベル | 基準値 | a（傾き） | ｂ（切片）
|  |  |  | #VALUE! | Level 1: WLC emission rate is 125% or more of the reference value. | [6 empty] | Between each level, it is evaluated by linear interpolation to the first decimal place. |  | 1.25 | 1.25 | 1 | 1.25 | -8 | 11 | 1 | 1.25 | -8 | 11
|  |  |  | #VALUE! | [9 empty] | 1.125 | 1.125 | 2 | 1.125 | -8 | 11 | 2 | 1.125 | -8 | 11
|  |  |  | #VALUE! | Level 3: WLC emission rate is 100% of the reference value. | [8 empty] | 1 | 1 | 3 | 1 | -4 | 7 | 3 | 1 | -4 | 7
|  |  |  | #VALUE! | [9 empty] | 0.75 | 0.75 | 4 | 0.75 | -4 | 7 | 4 | 0.75 | -4 | 7
|  |  |  | #VALUE! | Level 5: WLC emission rate is 50% or less of the reference value. | [8 empty] | 0.5 | 0.5 | 5 | 0.5 |  |  | 5 | 0.5
|  |  |  | Outline of env. efforts | [9 empty] | 暫定案(留保)
|  |  |  | Approximate calculation of WLC |  |  |  |  | kg-CO2eq/yr-㎡ |  |  |  |  | 0.95 | 1.05 | WLC排出率 ≧ 0.95（1.1） |  |  | 1.05 | WLC排出率 ≧ 1.05
[6 empty] | Construction | Repair, renewal/demolition | Operation | Total | Emission Rate |  |  | Score conversion by WLC emission rate | 0.9 | 1 | WLC排出率＝ 0.9（1.0） |  |  | 1 | WLC排出率＝ 1.0
N.A. |  |  |  |  | Ref. Bldg. | 18.22 | 20.11 | #VALUE! | #VALUE! | 100% |  | Score conversion＝ | #VALUE! | 0.75 | 0.75 | WLC排出率 ＝ 0.75 |  |  | 0.95 | WLC排出率 ＝ 0.95
[5 empty] | Eval. Bldg. | 18.22 | 20.11 | #VALUE! | #VALUE! | #VALUE! |  |  |  | 0.65 | 0.65 | WLC排出率 ＝ 0.65 |  |  | 0.75 | WLC排出率 ＝ 0.75
|  |  |  | 集合住宅 |  | 建設 | 修繕・更新・解体 | 運用 | Total | 排出率 |  |  | WLC排出率に基づくスコア換算 | 0.5 | 0.5 | WLC排出率 ≦ 0.5 |  |  | 0.6 | WLC排出率 ≦ 0.6
[5 empty] | 参照値 | 18.22 | 20.11 | #VALUE! | #VALUE! | 100% |  | 換算スコア＝ | #VALUE!
[5 empty] | 評価対象 | 18.22 | 20.11 | #VALUE! | #VALUE! | #VALUE!
|  | 2 | Consideration of Local Environment
|  | 2.1 | Air Pollution
[6 empty] | Weighting coef.(default) = |  | 0.25
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
1 |  |  |  | Level 1 | Gas and dust concentrations at sources of NOx, SOx and dust exceeds the emission standards set by the Air Pollution Control Law, the Guidelines for Small Capacity Low NOx Combustors (MOE) or local ordinances.
- |  |  |  | Level 2 | (No corresponding level)
3 |  |  |  | ■Level 3 | Gas and dust concentrations at sources of NOx, SOx and dust are reduced to below the emission standards*1 set by the Air Pollution Control Law, the Guidelines for Small Capacity Low NOx Combustors (MOE) or local ordinances.
4 |  |  |  | Level 4 | Gas and dust concentrations at sources of NOx, SOx and dust are considerably reduced to below the emission standards*2 set by the Air Pollution Control Law, the Guidelines for Small Capacity Low NOx Combustors (MOE) or local ordinances.
5 |  |  |  | Level 5 | No incineration equipment is used, and absolutely no atmospheric pollutants leave the virtual enclosed space boundary of the building to the outside.
0 | 0 |  |  | Outline of env. efforts
|  | 2.2 | Heat Island Effect
[6 empty] | Weighting coef.(default) = |  | 0.5
Min |  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
0 |  |  |  | Level 1 | 0 points in total from the table of the efforts to be evaluated.
1 |  |  |  | Level 2 | 1-5 points in total from the table of the efforts to be evaluated.
6 |  |  |  | ■Level 3 | 6-12 points in total from the table of the efforts to be evaluated.
13 |  |  |  | Level 4 | 13-19 points in total from the table of the efforts to be evaluated.
20 |  |  |  | Level 5 | 20 points or more in total from the table of the efforts to be evaluated.
|  |  |  | Outline of env. efforts |  |  |  |  | Note; Describe specific initiatives for each effort.
|  |  |  | Exposed area ratio |  | #DIV/0! | Exposed area Sb |  | Ws: Maximum width of the site perpendicular to the prevailing wind direction |  |  | Hb: Standard height
Building spacing index Rw
|  |  |  | Percentage of |  |  | Countermeasure area ratio | Green cover ratio | Water-covered area ratio | Evaporative surface ratio | Horizontal projection area ratio of medium and tall trees | High solar reflectance surface ratio | Retroreflective surface ratio
|  |  |  | appropriate ground surface |  | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  |  | appropriate roof top surface |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | appropriate exterior wall surface |  | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! |  | #DIV/0! | #DIV/0!
[7 empty] | subtotal area | green area | water surface | evaporative material covered area | horizontal projection areas of medium and tall trees | high solar reflectance material covered area | retroreflective material covered area
[5 empty] | Areas [㎡] | ground surface | 5000 | 0 | 0 |  | 0
[6 empty] | roof top |  | 0
[6 empty] | exterior wall | 0 | 0 |  | 0 |  |  | 0
[6 empty] | Total |  | 0 | 0 | 0 | 0 | 0 | 0
Efforts to be evaluated
Maｘ |  |  |  |  | 3 | Assessment Item |  |  | Description |  |  |  | Point allocation
2 |  |  |  | No.1 | 1 | I. Preliminary investigation of heat environment | 1) Preliminary investigation of the local heat environment |  | [1] Existing data such as data from nearby meteorological stations and regional meteorological observation data (AMEDAS data) was used to identify the wind environment, including directions, speeds and prevailing direction. (1 point) |  |  |  | 1～2
既存なし | [8 empty] | [2] In addition to [1] above, on-site measurements were taken, or a supplementary detailed investigation was performed using a wide-area environmental forecasting system based on wide-area meteorological data and topographical data. (2 points)
[9 empty] | [3] Inapplicable under CASBEE-BD/NC |  |  |  | ―
2 |  |  |  | No.2 | 1 | II. Thermal impact reduction in surrounding area | 2) Thermal impact reduction in surrounding area by facilitating the flow of air toward downwind areas |  | [1] Position and shape of the building are arranged in the planning to promote the flow of air downwind. |  |  |  | 1～2
The building has no practical impact on the flow of air downwind (1 point) The building does not obstruct the flow of air downwind (2 points)
3 |  |  |  | No.3 |  |  |  |  | [2] Exposed area of the building facing the prevailing summer winds is reduced. |  |  |  | 1～3
[9 empty] | Exposed area facing the prevailing wind direction is: 60% or more but less than 80% (1 point) 40% or more but less than 60% (2 points) Less than 40% (3 points) |  |  | #DIV/0!
3 |  |  |  | No.4 |  |  |  |  | [3] Height, shape and spacing of building are arranged to recover the flow of air. |  |  |  | 1～3
[9 empty] | Building spacing index Rw is: 0.3 or more but less than 0.4 (1 point) 0.4 or more but less than 0.5 (2 points) 0.5 or more (3 points) |  |  | Rw=
3 |  |  |  | No.5 |  |  | 3) Consider ground surface coverage to reduce thermal impact beyond the site |  | [1] Ground covering materials are used to reduce thermal impact. |  |  |  | 1～3
[9 empty] | Percentage of ground covered with appropriate materials is: 15% or more but less than 30% (1 point) 30% or more but less than 45% (2 points) 45% or more (3 points) |  |  | Countermeasure area ratio=0%
3 |  |  |  | No.6 | 1 |  | 4) Consider the building cladding materials to reduce thermal impact beyond the site |  | [1] Rooftop greenery system or high reflective roof material is used to reduce thermal impact. |  |  |  | 1～3
[9 empty] | Percentage of roof covered with appropriate system/material is: Less than 20% (1 point) 20% or more but less than 40% (2 points) 40% or more (3 points) |  |  | #DIV/0!
3 |  |  |  | No.7 | 1 |  |  |  | [2] Appropriate exterior wall materials are used to reduce thermal impact. |  |  |  | 1～3
[9 empty] | Percentage of exterior walls covered with appropriate material is: Less than 10% (1 point) 10% or more but less than 20% (2 points) 20% or more (3 points) |  |  | #DIV/0!
3 |  |  |  | No.8 | 1 |  | 5) Reduce atmospheric emission of heat from building equipment |  | [1] Appropriate measures to prevent heat loss via exterior walls/windows and to improve energy efficiency for HVAC systems have been implemented. |  |  |  | 1～3
Score (results) in the "LR1 Energy" assessment is: 3.0 or more but less than 4.0 (1 point) 4.0 or more but less than 4.5 (2 points) 4.5 or more (3 points)
3 |  |  |  | No.9 | 1 |  |  |  | [2] Air temperature increase is reduced by measures such as cooling of waste heat emitted from building service systems. |  |  |  | 1～3
Measures established to control air temperature increase are: at standard level (1 point) at intermediate level (2 points) at advanced level (3 points)
2 |  |  |  | No.10 |  | III. Confirmation of effects | 6) Use simulations or other means to confirm effects in mitigating deterioration of the heat environment |  | [1] Building form and positioning, relative to wind direction, were considered at the desk plan stage (desktop prediction). (1 point) |  |  |  | 1～2
[2] Numerical simulation of fluid flow, or other methods, was used for the current situation and the planned building, considering topography of the site area, the building and surrounding green space, to predict impact. (2 points)
|  |  |  | Total | 6 | points | [6 empty] | 27
|  | 2.3 | Load on Local Infrastructure
2.3.1 Reduction of Rain water Discharge Loads
[6 empty] | Weighting coef.(default) = |  | 0.25
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt <If there are administrative guidelines> |  |  |  |  | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt <If there are no administrative guidelines>
- |  |  |  | Level 1 | (No corresponding level)
- |  |  |  | Level 2 | (No corresponding level)
3 |  |  |  | ■Level 3 | Measures to control rainwater runoff are being implemented on the scale instructed. |  |  |  |  | No measures to control rainwater runoff have been implemented.
4 |  |  |  | Level 4 | Level 3 is satisfied, and measures are being implemented to control rainwater runoff, but Level 5 is not satisfied. |  |  |  |  | Measures are being implemented to control rainwater runoff, but Level 5 is not satisfied.
5 |  |  |  | Level 5 | Level 3 is satisfied, and the site has secured the basic rain stock capacity necessary for 100 mm/hour rainfall indicated in the "Technology Standard for Rainwater Harvesting" of the Architectural Institute of Japan.
0 | 0 |  |  | Outline of env. efforts
2.3.2 Sewage Load Suppression
[6 empty] | Weighting coef.(default) = |  | 0.25
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
- |  |  |  | Level 1 | (No corresponding level)
- |  |  |  | Level 2 | (No corresponding level)
3 |  |  |  | ■Level 3 | The Water Pollution Control Law, the Sewerage Law or the discharge standards set by local authorities etc., whichever is the most stringent, is satisfied.
4 |  |  |  | Level 4 | Discharge standards are satisfied, and further special measures have been used for better control of sewage loads.
- |  |  |  | Level 5 | (No corresponding level)
0 | 0 |  |  | Outline of env. efforts
2.3.3 Traffic Load Control
[6 empty] | Weighting coef.(default) = |  | 0.25
Min |  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
0 |  |  |  | Level 1 | 0 points in total from the table of the efforts to be evaluated.
1 |  |  |  | Level 2 | 1 point in total from the table of the efforts to be evaluated.
2 |  |  |  | ■Level 3 | 2 points in total from the table of the efforts to be evaluated.
3 |  |  |  | Level 4 | 3 points in total from the table of the efforts to be evaluated.
4 |  |  |  | Level 5 | 4 points or more in total from the table of the efforts to be evaluated.
|  |  |  | Outline of env. efforts |  |  |  |  | Note; Describe specific initiatives for each effort.
Efforts to be evaluated
Max |  |  |  |  | 3 | Assessment Item |  |  | Description |  |  |  | Point allocation
1 |  |  |  | No.1 |  | I. Efforts related to use of bicycles (use of alternative means of transport) |  |  | 1) Provision of an appropriate number of cycle parking spaces (including motorcycle spaces) for building users, and consideration for the convenience of cycle park users (ease of entry and egress, placement in a convenient location, etc.). |  |  |  | 1
1 |  |  |  | No.2 | 1 |  |  |  | 2) Other initiatives (State specific initiatives in the outline of env. efforts.) |  |  |  | 1
1 |  |  |  | No.3 |  | II. Efforts to provide car parking space |  |  | 1) Provision of an appropriate number of car parking spaces (as a measure to avoid parking on roads, and congestion of nearby roads). |  |  |  | 1
1 |  |  |  | No.4 | 1 |  |  |  | 2) Provision of parking facilities for unloading goods vehicles (residential buildings are not applicable). |  |  |  | 1
1 |  |  |  | No.5 |  |  |  |  | 3) Consideration of the position, form and number of parking lot approach roads (entry and exit) (to contribute to relieving congestion of local roads). |  |  |  | 1
1 |  |  |  | No.6 |  |  |  |  | 4) Other initiatives (State specific initiatives in the outline of env. efforts.) |  |  |  | 1
|  |  |  | Total | 2 | points | [6 empty] | 6
2.3.4 Reduction of Waste Treatment Loads
既存は住の基準あり | [5 empty] | Weighting coef.(default) = |  | 0.25
Min | Min |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct |  |  | 7000 | Apt |  |  |  | 0
0 | 0 |  |  | Level 1 | 0-1 point in total from the table of the efforts to be evaluated.
2 | 2 |  |  | Level 2 | 2 points in total from the table of the efforts to be evaluated.
3 | 3 |  |  | ■Level 3 | 3 points in total from the table of the efforts to be evaluated.
4 | 4 |  |  | Level 4 | 4 points in total from the table of the efforts to be evaluated.
5 | 5 |  |  | Level 5 | 5 points or more in total from the table of the efforts to be evaluated.
|  |  |  | Outline of env. efforts |  |  |  |  | Note; Describe specific initiatives for each effort.
Efforts to be evaluated
Max |  |  |  |  | 3 | Assessment Item |  |  | Description |  |  |  | Point allocation
1 |  |  |  | No.1 | 1 | I. Estimation of types and quantities of waste |  |  | 1) The types and quantities of waste generated on the site (interior and exterior) on a day-to-day basis have been estimated to assist in planning measures to reduce the waste processing load. |  |  |  | 1
1 |  |  |  | No.2 | 1 | II. Provision of space and equipment to encourage separate collection |  |  | 2) Interior and exterior stock space has been planned that will allow sorted collection of many varieties of waste. |  |  |  | 1
1 |  |  |  | No.3 |  |  |  |  | 3) Interior and exterior waste sorting and collection containers and boxes have been planned. |  |  |  | 1
1 |  |  |  | No.4 |  |  |  |  | 4) Planned collection of valuable materials has been planned (group collections, etc.). |  |  |  | 1
新築なし |  |  |  | No.5 |  |  |  |  | 5) Inapplicable under CASBEE-BD/NC |  |  |  | ―
1 |  |  |  | No.6 | 1 | III. Installation of equipment for waste reduction, compaction or composting |  |  | 6) Measures are planned to reduce, compact and compost organic garbage (home processing and composting etc. of organic waste). |  |  |  | 1
1 |  |  |  | No.7 |  |  |  |  | 7) Reduction and compaction of bottles, cans etc. are planned. |  |  |  | 1
|  |  |  | Total | 3 | points |  | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct： | 3 | Apt： | 3 |  | 6
|  | 3 | Consideration of Surrounding Environment
|  | 3.1 | Noise, Vibration & Odor
3.1.1 Noise
[6 empty] | Weighting coef.(default) = |  | 0.33333
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt | [6 empty] | Remarks
1 |  |  |  | Level 1 | Noise level exceeds the current regulation standard*1 specified under the Noise Regulation Law or the Large-Scale Retail Stores Location Law or regulations such as local ordinances. | [6 empty] | Select "Level 3" if the building has no designated facilities subject to the regulation.
- |  |  |  | Level 2 | (No corresponding level)
3 |  |  |  | ■Level 3 | Noise level is at or below the current regulation standard*1 specified under the Noise Regulation Law or the Large-Scale Retail Stores Location Law or regulations such as local ordinances.
- |  |  |  | Level 4 | (No corresponding level)
5 |  |  |  | Level 5 | Noise level is significantly below*2 the current regulation standard*1 specified under the Noise Regulation Law or the Large-Scale Retail Stores Location Law or regulations such as local ordinances.
0 | 0 |  |  | Outline of env. efforts
*1 Take the current values of the regulation standard, and evaluate facilities accordingly, even if they were installed before the current values came into effect (evaluate for day, morning, evening and night).
*2 Level 5 applies to noise level at or below [current standard value -10 dB] throughout the day.
Standard noise levels specified under the Noise Regulation Law
A condition of assessment is that the standards must be satisfied for all the measurement times, namely day (8am - 7pm), morning and evening (6am - 8am, 7pm - 10pm) and night (10pm - 6am).
[5 empty] | Type 1 zones |  |  | Type 2 zones
[5 empty] | Day | Morning & evening | Night | Day | Morning & evening | Night
|  |  |  | Level 1 | Not adequate for level 3 | Not adequate for level 3 | Not adequate for level 3 | Not adequate for level 3 | Not adequate for level 3 | Not adequate for level 3
Level 2
|  |  |  | Level 3 | Not exceeding 45 dB | Not exceeding 40 dB | Not exceeding 40 dB | Not exceeding 50 dB | Not exceeding 45 dB | Not exceeding 45 dB
Level 4
|  |  |  | Level 5 | Not exceeding 35 dB | Not exceeding 30 dB | Not exceeding 30 dB | Not exceeding 40 dB | Not exceeding 35 dB | Not exceeding 35 dB
[5 empty] | Type 3 zones |  |  | Type 4 zones
[5 empty] | Day | Morning & evening | Night | Day | Morning & evening | Night
|  |  |  | Level 1 | Not adequate for level 3 | Not adequate for level 3 | Not adequate for level 3 | Not adequate for level 3 | Not adequate for level 3 | Not adequate for level 3
Level 2
|  |  |  | Level 3 | Not exceeding 60 dB | Not exceeding 55 dB | Not exceeding 50 dB | Not exceeding 70 dB | Not exceeding 60 dB | Not exceeding 55 dB
Level 4
|  |  |  | Level 5 | Not exceeding 50 dB | Not exceeding 45 dB | Not exceeding 40 dB | Not exceeding 60 dB | Not exceeding 50 dB | Not exceeding 45 dB
3.1.2 Vibration
[6 empty] | Weighting coef.(default) = |  | 0.33333
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt | [6 empty] | Remarks
1 |  |  |  | Level 1 | Vibration level exceeds the current regulation standard*1 specified under the Vibration Regulation Law or regulations such as local ordinances. | [6 empty] | Inapplicable (N.A.) if the building is not located in the designated area, or has no designated facilities within the designated area subject to the regulation.
- |  |  |  | Level 2 | (No corresponding level)
3 |  |  |  | ■Level 3 | Vibration level is at or below the current regulation standard*1 specified under the Vibration Regulation Law or regulations such as local ordinances.
- |  |  |  | Level 4 | (No corresponding level)
5 |  |  |  | Level 5 | Vibration level is significantly below*2 the current regulation standard*1 specified under the Vibration Regulation Law or regulations such as local ordinances.
0 | 0 |  |  | Outline of env. efforts
*1 Take the current values of the regulation standard, and evaluate facilities accordingly, even if they were installed before the current values came into effect (evaluate for both day and night).
*2 For level 5, vibration should be limited to below [current standard value -5 dB] (for both day and night).
Standard Values from the Vibration Regulation Law
A condition of assessment is that the standards must be satisfied for all the measurement times, namely day (8am ~ 7pm) and night (7pm ~ 8am).
[5 empty] | Type 1 zones |  |  | Type 1 zones
[5 empty] | Day | Night |  | Day | Night
|  |  |  | Level 1 | Not adequate for level 3 | Not adequate for level 3 |  | Not adequate for level 3 | Not adequate for level 3
Level 2
|  |  |  | Level 3 | Not exceeding 60 dB | Not exceeding 55 dB |  | Not exceeding 65 dB | Not exceeding 60 dB
Level 4
|  |  |  | Level 5 | Not exceeding 55 dB | Not exceeding 50 dB |  | Not exceeding 60 dB | Not exceeding 55 dB
3.1.3 Odor
[6 empty] | Weighting coef.(default) = |  | 0.33333
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt | [6 empty] | Remarks
1 |  |  |  | Level 1 | Vibration level exceeds the current regulation standard*1 specified under the Vibration Regulation Law or regulations such as local ordinances. | [6 empty] | Inapplicable (N.A.) if no designated substances are treated, or if the building has no designated facilities subject to the regulation.
- |  |  |  | Level 2 | (No corresponding level)
3 |  |  |  | ■Level 3 | Vibration level is at or below the current regulation standard*1 specified under the Vibration Regulation Law or regulations such as local ordinances.
- |  |  |  | Level 4 | (No corresponding level)
- |  |  |  | Level 5 | Vibration level is significantly below*2 the current regulation standard*1 specified under the Vibration Regulation Law or regulations such as local ordinances.
0 | 0 |  |  | Outline of env. efforts
|  | 3.2 | Wind/Sand Damage & Sunlight Obstruction
3.2.1 Restriction of Wind Damage
[6 empty] | Weighting coef.(default) = |  | 0.7
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt | [6 empty] | Remarks
1 |  |  |  | Level 1 | No preliminary study or was performed about the creation of strong wind spots*1 and no countermeasures*2 were taken against wind hazard. | [6 empty] | Select "Level 3" if the building applies no particular measures in the absence of a mandate based on law, regulation of administrative instruction, or of demands from the local area.
2 |  |  |  | Level 2 | A preliminary study has been performed and measures taken to avoid or reduce wind hazard, but there has been no assessment. Alternatively, wind strength grade has been evaluated on the basis of a desktop forecast*3, and wind strength has been worsened in some areas, or there are measurement points at which the wind environment rank for the sight has been lowered.
3 |  |  |  | ■Level 3 | A preliminary study has been performed and measures taken to avoid or reduce wind hazard*4. Then, the wind strength grade has been evaluated on the basis of a desktop forecast*3, and the results show that wind strength has not worsened. Alternatively, rank assessment has been performed on the basis of wind environment assessment indices*5, and the results indicate that a wind environment with suitable rank for the location has been achieved.
4 |  |  |  | Level 4 | A preliminary study or prevention planning has been performed and measures taken to avoid or reduce wind hazard, followed by a rank assessment*5 has been performed on the basis of wind environment assessment indices. Results indicate that the wind environment in some parts is better than usual for the location.
5 |  |  |  | Level 5 | A preliminary study or prevention planning has been performed and measures taken to avoid or reduce wind hazard, followed by a rank assessment*5 has been performed on the basis of wind environment assessment indices. Results indicate that the wind environment is better than usual for the location.
0 | 0 |  |  | Outline of env. efforts |  |  |  |  | Note; State if there is no mandate or demands against wind damage or if voluntary initiatives are not evaluated.
|  |  |  | 3.2.2 Control of Sand and Dust |  |  |  | <N.A.>
[6 empty] | Weighting coef.(default) = |  | 0
Min |  |  |  | 3 | Sch(E.S./J.H.S./H.S.)
0 |  |  |  | Level 1 | 0 points in total from the table of the efforts to be evaluated.
1 |  |  |  | Level 2 | Insufficient level of measures for schoolyard dust control is established. (1 point in total)
2 |  |  |  | ■Level 3 | Standard level of measures for schoolyard dust control is established. (2 points in total)
3 |  |  |  | Level 4 | More than sufficient level of measures for schoolyard dust control are established.
4 |  |  |  | Level 5 | (3 points in total)
|  |  |  | Outline of env. efforts |  |  |  |  | Note; Describe specific initiatives for each effort.
Efforts to be evaluated
Max |  |  |  |  | 3 | Assessment Item |  |  | Description |  |  |  | Point allocation
2 |  |  |  | No.1 | 2 | I. Measures to control airborne dispersion of dust from schoolyard |  |  | 1) Dust shield trees or nets surrounding the school perimeter. |  |  |  | 1
[9 empty] | 2) Structures surrounding the school perimeter. |  |  |  | 2
4 |  |  |  | No.2 |  | II. Dust-proofing measures for schoolyard surface |  |  | 1) Sprinkler system |  |  |  | 1
[9 empty] | 2) Dust-proof paving |  |  |  | 2
[9 empty] | 3) Dust-proof paving/lawn covering |  |  |  | 4
|  |  |  | Total | 2 | points | [6 empty] | 6
3.2.3 Restriction of Sunlight Obstruction
[6 empty] | Weighting coef.(default) = |  | 0.3
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
1 | 1 |  |  | Level 1 | Not adequate for Level 3.
- | 2 |  |  | Level 2 | (No corresponding level)
3 | 3 |  |  | ■Level 3 | Shade regulations are satisfied, or there are no shade regulations applicable to the site.
4 | 4 |  |  | Level 4 | A standard one rank* above the shade regulations is satisfied.
- | 5 |  |  | Level 5 | (No corresponding level) the one stricter
0 | 0 |  |  | Outline of env. efforts |  |  |  |  | Note; State if there is no regulations against sunlight obstruction.
*"One rank above" for sunlight obstruction means that, for example, in an area where the shade regulation limits shade on adjacent commercial areas to 5 hours/3 hours (at 5 m, 10 m), the next higher standard is for residential areas, set at 4/2.5 hours.
|  | 3.3 | Light Pollution
3.3.1 Outdoor Illumination and Light that Spills from Interiors
[6 empty] | Weighting coef.(default) = |  | 0.7
Min |  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
0 |  |  |  | Level 1 | 0 points in total from the table of the efforts to be evaluated.
1 |  |  |  | Level 2 | 1 point in total from the table of the efforts to be evaluated.
2 |  |  |  | ■Level 3 | 2 points in total from the table of the efforts to be evaluated.
3 |  |  |  | Level 4 | 3 points in total from the table of the efforts to be evaluated.
4 |  |  |  | Level 5 | 4 points in total from the table of the efforts to be evaluated.
|  |  |  | Outline of env. efforts |  |  |  |  | Note; Describe specific initiatives for each effort.
Efforts to be evaluated
Max |  |  |  |  | 3 | Description | [6 empty] | Point allocation
2 |  |  |  | No.1 |  | 1) Outdoor illumination and light that spills from interiors | [6 empty] | 1～2
Only some of the checklist points of the "Light Pollution Countermeasure Guidelines" are satisfied. (1 point)
A majority of the checklist points of the "Light Pollution Countermeasure Guidelines" are satisfied. (2 points)
2 |  |  |  | No.2 | 2 | 2) Countermeasures against light pollution from billboard lighting | [6 empty] | 1～2
Billboard lighting satisfies some of the considerations in "Considerations for Billboard Illumination." (1 point)
A majority of the considerations in "Considerations for Billboard Illumination" are satisfied, or there is no billboard lighting. (2 points)
|  |  |  | Total | 2 | points | [6 empty] | 4
3.3.2 Measures for Reflected Solar Glare from Building Walls
[6 empty] | Weighting coef.(default) = |  | 0.3
|  |  |  | 3 | Off,Sch,Rtl,Rst,Hal,Hsp,Htl,Fct,Apt
- |  |  |  | Level 1 | (No corresponding level)
- |  |  |  | Level 2 | (No corresponding level)
3 |  |  |  | ■Level 3 | Not adequate for Level 4.
4 |  |  |  | Level 4 | Measures for reducing reflected glare from building walls (including glass surfaces) are taken.
5 |  |  |  | Level 5 | In addition to efforts required for Level 4, further advanced measures such as confirming a significant reduction effect due to simulation practice are taken.
0 | 0 |  |  | Outline of env. efforts
Note on I55: 敷地面積

## WLC
CASBEE for Building Design (New Construction) 2024 Edition | [8 empty] | n Manual: |  |  | CASBEE for Building Design (New Construction) 2024 Edition
XXX Building | [8 empty] | n Software: |  |  | CASBEE-BD_NCe_2024_v1.21
Whole Life Carbon Calculation Sheet （For Standard calculation）
[10 empty] | Evaluated Bldg. |  | Reference Bldg. |  | S造 | RC造 | SRC造 | 木造
1. GHG Emissions Related to Construction | [13 empty] | LCCO2用床面積 |  | 合計 | 7000
| 1-1. Conversion of Assessment Results to GHG emission | [8 empty] | kg-CO2eq/yr-m2 |  | kg-CO2eq/yr-m2 |  | Offices | 7000
|  | Q2/2.2.1 Service Life of Structural Frame Materials |  | Floor area comp |  | Level 3 | Level 4 | Level 5 | Score | GHG emission | Score | GHG emission |  | 0 | 0
|  |  | Office | 1 |  | 18.22 | 18.22 | 18.22 | 3 | 18.22 | 3 | 18.22 |  | Schools | 0
|  |  | School | 0 |  | 18.59 | 18.59 | 18.59 | 3 | 18.59 | 3 | 18.59 |  | 0 | 0 |  |  | Sch
|  |  | Retailers | 0 |  | 22.88 | 22.88 | 22.88 | 3 | 22.88 | 3 | 22.88 |  | 0 | 0 |  |  | 0
|  |  | Restaurants | 0 |  | 22.88 | 22.88 | 22.88 | 3 | 22.88 | 3 | 22.88 |  | 0 | 0
|  |  | Halls | 0 |  | 17.92 | 17.92 | 17.92 | 3 | 17.92 | 3 | 17.92 |  | 0 | 0
|  |  | Factories | 0 |  | 30.17 | 30.17 | 30.17 | 3 | 30.17 | 3 | 30.17 |  | Retailers | 0
|  |  | Hospitals | 0 |  | 18.17 | 18.17 | 18.17 | 3 | 18.17 | 3 | 18.17 |  | 0 | 0
|  |  | Hotels | 0 |  | 19.72 | 19.72 | 19.72 | 3 | 19.72 | 3 | 19.72 |  | Restaurants | 0
|  |  | Apartments | 0 |  | 33.92 | 16.96 | 11.31 | 3 | 33.92 | 3 | 33.92 |  | Halls | 0
[14 empty] | 0 | 0
|  | Structure of the evaluated building |  | RC | [9 empty] | 0 | 0
|  | LR2.2.2 Existing structural frame |  | 0% | [6 empty] | 0% |  |  | Factories | 0 | ㎡ Area subjected for energy efficiency calc | 0
|  | LR2.2.3 Recycled materials (Use of blast furnace cement) |  | 0% | [6 empty] | 0% |  |  | Hospitals | 0
[14 empty] | Hotels | 0
[14 empty] | Non-Apartment Subtotal | 7000
[14 empty] | Apartments | 0
| Lifespan |  | Office | 1 |  | 60 | 60 | 60 | 3 | 60 | 3 | 60 |  | Office, |  |  | Office,
|  |  | School | 0 |  | 60 | 60 | 60 | 3 | 0 | 3 | 0
|  |  | Retailers | 0 |  | 30 | 30 | 30 | 3 | 0 | 3 | 0
|  |  | Restaurants | 0 |  | 30 | 30 | 30 | 3 | 0 | 3 | 0
|  |  | Halls | 0 |  | 60 | 60 | 60 | 3 | 0 | 3 | 0
|  |  | Factories | 0 |  | 30 | 30 | 30 | 3 | 0 | 3 | 0
|  |  | Hospitals | 0 |  | 60 | 60 | 60 | 3 | 0 | 3 | 0
|  |  | Hotels | 0 |  | 60 | 60 | 60 | 3 | 0 | 3 | 0
|  |  | Apartments | 0 |  | 30 | 60 | 90 | 3 | 0 | 3 | 0
|  |  | Total |  |  | 60 |  |  |  | 60years(Office,) | 60 | 60years(Office,) |  | Office, |  |  | Office,
| Quantities of Representative Materials | [5 empty] | Existing Structure 100% | Blast furnace cement100%
|  | Office | Regular concrete | 1 |  | 0.696 | 0 | 0 |  | 0.696 |  | 0.696 | m3/m2
|  |  | Blast furnace cement concrete | 1 |  | 0 | 0 | 0.696 |  | 0 |  | 0 | m3/m2
|  |  | Formwork | 1 |  | 0.6675 | 0 | 0.6675 |  | 0.6675 |  | 0.6675 | m2/m2
|  |  | Reinforcing bars | 1 |  | 0.078 | 0 | 0.078 |  | 0.078 |  | 0.078 | t/m2
|  |  | Steel frame | 1 |  | 0.1 | 0 | 0.1 |  | 0.1 |  | 0.1 | t/m2
|  |  | Deck plate | 1 |  | 0 | 0 | 0 |  | 0 |  | 0 | m2/m2
|  | School | Regular concrete | 0 |  | 0.958 | 0 | 0 |  | 0.958 |  | 0.958 | m3/m2
|  |  | Blast furnace cement concrete | 0 |  | 0 | 0 | 0.958 |  | 0 |  | 0 | m3/m2
|  |  | Formwork | 0 |  | 0.9725 | 0 | 0.9725 |  | 0.9725 |  | 0.9725 | m2/m2
|  |  | Reinforcing bars | 0 |  | 0.11 | 0 | 0.11 |  | 0.11 |  | 0.11 | t/m2
|  |  | Steel frame | 0 |  | 0.078 | 0 | 0.078 |  | 0.078 |  | 0.078 | t/m2
|  |  | Deck plate | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | m2/m2
|  | Retailers | Regular concrete | 0 |  | 0.307 | 0 | 0 |  | 0.307 |  | 0.307 | m3/m2
|  |  | Blast furnace cement concrete | 0 |  | 0 | 0 | 0.307 |  | 0 |  | 0 | m3/m2
|  |  | Formwork | 0 |  | 0.4025 | 0 | 0.4025 |  | 0.4025 |  | 0.4025 | m2/m2
|  |  | Reinforcing bars | 0 |  | 0.053 | 0 | 0.053 |  | 0.053 |  | 0.053 | t/m2
|  |  | Steel frame | 0 |  | 0.071 | 0 | 0.071 |  | 0.071 |  | 0.071 | t/m2
|  |  | Deck plate | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | m2/m2
|  | Restaurants | Regular concrete | 0 |  | 0.307 | 0 | 0 |  | 0.307 |  | 0.307 | m3/m2
|  |  | Blast furnace cement concrete | 0 |  | 0 | 0 | 0.307 |  | 0 |  | 0 | m3/m2
|  |  | Formwork | 0 |  | 0.4025 | 0 | 0.4025 |  | 0.4025 |  | 0.4025 | m2/m2
|  |  | Reinforcing bars | 0 |  | 0.053 | 0 | 0.053 |  | 0.053 |  | 0.053 | t/m2
|  |  | Steel frame | 0 |  | 0.071 | 0 | 0.071 |  | 0.071 |  | 0.071 | t/m2
|  |  | Deck plate | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | m2/m2
|  | Halls | Regular concrete | 0 |  | 0.862 | 0 | 0 |  | 0.862 |  | 0.862 | m3/m2
|  |  | Blast furnace cement concrete | 0 |  | 0 | 0 | 0.862 |  | 0 |  | 0 | m3/m2
|  |  | Formwork | 0 |  | 1.0225 | 0 | 1.0225 |  | 1.0225 |  | 1.0225 | m2/m2
|  |  | Reinforcing bars | 0 |  | 0.1 | 0 | 0.1 |  | 0.1 |  | 0.1 | t/m2
|  |  | Steel frame | 0 |  | 0.059 | 0 | 0.059 |  | 0.059 |  | 0.059 | t/m2
|  |  | Deck plate | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | m2/m2
|  | Factories | Regular concrete | 0 |  | 0.669 | 0 | 0 |  | 0.669 |  | 0.669 | m3/m2
|  |  | Blast furnace cement concrete | 0 |  | 0 | 0 | 0.669 |  | 0 |  | 0 | m3/m2
|  |  | Formwork | 0 |  | 0.5575 | 0 | 0.5575 |  | 0.5575 |  | 0.5575 | m2/m2
|  |  | Reinforcing bars | 0 |  | 0.08 | 0 | 0.08 |  | 0.08 |  | 0.08 | t/m2
|  |  | Steel frame | 0 |  | 0.077 | 0 | 0.077 |  | 0.077 |  | 0.077 | t/m2
|  |  | Deck plate | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | m2/m2
|  | Hospitals | Regular concrete | 0 |  | 0.812 | 0 | 0 |  | 0.812 |  | 0.812 | m3/m2
|  |  | Blast furnace cement concrete | 0 |  | 0 | 0 | 0.812 |  | 0 |  | 0 | m3/m2
|  |  | Formwork | 0 |  | 0.8075 | 0 | 0.8075 |  | 0.8075 |  | 0.8075 | m2/m2
|  |  | Reinforcing bars | 0 |  | 0.089 | 0 | 0.089 |  | 0.089 |  | 0.089 | t/m2
|  |  | Steel frame | 0 |  | 0.066 | 0 | 0.066 |  | 0.066 |  | 0.066 | t/m2
|  |  | Deck plate | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | m2/m2
|  | Hotels | Regular concrete | 0 |  | 0.816 | 0 | 0 |  | 0.816 |  | 0.816 | m3/m2
|  |  | Blast furnace cement concrete | 0 |  | 0 | 0 | 0.816 |  | 0 |  | 0 | m3/m2
|  |  | Formwork | 0 |  | 1.04 | 0 | 1.04 |  | 1.04 |  | 1.04 | m2/m2
|  |  | Reinforcing bars | 0 |  | 0.093 | 0 | 0.093 |  | 0.093 |  | 0.093 | t/m2
|  |  | Steel frame | 0 |  | 0.084 | 0 | 0.084 |  | 0.084 |  | 0.084 | t/m2
|  |  | Deck plate | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | m2/m2
|  | Apartments | Regular concrete | 0 |  | 0.75 | 0 | 0 |  | 0.75 |  | 0.75 | m3/m2
|  |  | Blast furnace cement concrete | 0 |  | 0 | 0 | 0.75 |  | 0 |  | 0 | m3/m2
|  |  | Formwork | 0 |  | 1.0425 | 0 | 1.0425 |  | 1.0425 |  | 1.0425 | m2/m2
|  |  | Reinforcing bars | 0 |  | 0.136 | 0 | 0.136 |  | 0.136 |  | 0.136 | t/m2
|  |  | Steel frame | 0 |  | 0.052 | 0 | 0.052 |  | 0.052 |  | 0.052 | t/m2
|  |  | Deck plate | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | m2/m2
| ◆ | Total | Regular concrete | m3/m2 | [5 empty] | 0.696 |  | 0.696
|  |  | Blast furnace cement concrete | m3/m2 | [5 empty] | 0 |  | 0
|  |  | Formwork | m2/m2 | [5 empty] | 0.6675 |  | 0.6675
|  |  | Reinforcing bars | t/m2 | [5 empty] | 0.078 |  | 0.078
|  |  | Steel frame | t/m2 | [5 empty] | 0.1 |  | 0.1
|  |  | Deck plate | m2/m2 | [5 empty] | 0 |  | 0
1-2. Addition of GHG emissions related to equipment installation (to [3])
|  |  |  | Installed capacity |  |  | GHG intensity
|  |  | Solar power generation system | 0 | kW |  | 19.34 | kg-CO2eq/yr-kW |  | 0
|  |  | Battery | 0 | kWh |  | 3.33 | kg-CO2eq/yr-kWh |  | 0
|  |  | Lifespan of evaluated building | 60 |  | Office, assumed (same as 2-2)
| 1-3. Subtotal | [7 empty] | [2] | 18.22 | [1] | 18.22
[9 empty] | [3] | 18.22
2. GHG Emissions Related to Repair, Renewal and Demolition
| 2-1. Conversion of Assessment Results to GHG emission | [8 empty] | kg-CO2eq/yr-m2 |  | kg-CO2eq/yr-m2
|  | Q2/2.2.1 Service Life of Structural Frame Materials |  | Floor area comp |  | Level 3 | Level 4 | Level 5 | Score | GHG emission | Score | GHG emission
|  |  | Office | 1 |  | 20.11 | 20.11 | 20.11 | 3 | 20.11 | 3 | 20.11
|  |  | School | 0 |  | 14.59 | 14.59 | 14.59 | 3 | 14.59 | 3 | 14.59
|  |  | Retailers | 0 |  | 8.71 | 8.71 | 8.71 | 3 | 8.71 | 3 | 8.71
|  |  | Restaurants | 0 |  | 8.71 | 8.71 | 8.71 | 3 | 8.71 | 3 | 8.71
|  |  | Halls | 0 |  | 17.54 | 17.54 | 17.54 | 3 | 17.54 | 3 | 17.54
|  |  | Factories | 0 |  | 9.96 | 9.96 | 9.96 | 3 | 9.96 | 3 | 9.96
|  |  | Hospitals | 0 |  | 19.66 | 19.66 | 19.66 | 3 | 19.66 | 3 | 19.66
|  |  | Hotels | 0 |  | 22.25 | 22.25 | 22.25 | 3 | 22.25 | 3 | 22.25
|  |  | Apartments | 0 |  | 10.89 | 12.24 | 12.55 | 3 | 10.89 | 3 | 10.89
2-2. Addition of GHG emissions related to equipment installation (to [3])
|  |  |  | Installed capacity |  |  | GHG intensity
|  |  | Solar power generation system | 0 | kW |  | 39.0067 | kg-CO2eq/yr-kW |  | 0
|  |  | Battery | 0 | kWh |  | 6.7023 | kg-CO2eq/yr-kWh |  | 0
| 2-3. Subtotal | [7 empty] | [2] | 20.11 |  | 20.11
[9 empty] | [3] | 20.11
3. GHG Emissions Related to Operation Energy | [9 empty] | kg-CO2eq/yr-m2 |  | kg-CO2eq/yr-m2 |  | N.A.
| 3-1. Building-related Initiatives [2] |  |  | Floor area |  | Prim. Energy [GJ/yr] |  | GHG conversion coefficient |  | #VALUE! | Ref. bldg. [1] | #VALUE!
|  |  |  | ㎡ |  | Ref. bldg. [1] | Eval. bldg. [2] | kg-CO2eq/MJ
|  |  | Building except Apt. area | 7000 |  | 10850 | 5425 | #VALUE! |  | #VALUE! |  | #VALUE!
|  |  | Apt. dwelling area (dwelling units total) | 0 |  | 0 | 0 | #VALUE! |  | 0 |  | 0
|  |  | Apt. Common area | 0 |  | 0 | 0 | #VALUE! |  | 0 |  | 0
|  |  | subtotal | 7000
| 3-2. Above Initiatives + Other On-site Measures [3] | [5 empty] | Eval. bldg. [3] |  |  | #VALUE!
|  |  | Building except Apt. area | 7000 |  |  | 2712.5 | #VALUE! |  | #VALUE!
|  |  | Apt. dwelling area (dwelling units total) | 0 |  |  | 0 | #VALUE! |  | 0
|  |  | Apt. Common area | 0 |  |  | 0 | #VALUE! |  | 0
|  |  | subtotal | 7000
|  |  | 0 | 売電分
| 3-3. <Ref.>Above Initiatives + Other Off-site Measures [4] | [5 empty] | Eval. bldg. [4] |  | [4] | #VALUE!
|  |  | Building except Apt. area | 7000 |  |  | 2712.5 | #VALUE! |  | #VALUE!
Apt. (same GHG as [3])
4. Calculation of WLC (Standard Calculation) | [9 empty] | kg-CO2eq/yr-m2 |  | kg-CO2eq/yr-m2
[10 empty] | GHG emission |  | GHG emission
| Construction | [8 empty] | 18.22 |  | 18.22
| Repair, Renewal and Demolition | [8 empty] | 20.11 |  | 20.11
| Operation | [8 empty] | #VALUE! |  | #VALUE!
| Total | [8 empty] | #VALUE! |  | #VALUE!

## SDGs
Built Environment SDGs Checklist | [8 empty] | ■Building Name | XXX Building
implemented
|  |  | Whether or not this checklist is implemented: | implemented |  | Version | CASBEE-BD_NCe_2024_v1.21 |  |  | n Assessment Manual : |  |  | CASBEE for Building Design (New Construction) 2024 Edition | not implemented
[14 empty] | 〇 | [9 empty] | 建築環境 SDGs 評価素点 | CASBEE評価の点数
SDGs/ Targets | Assessment items of the Built Environment SDGs Checklist |  |  |  | Efforts to be assessed | Bldg. type | Remarks (referred items from CASBEE) | Not engaging (1 pt) | Engaging (2 pts) | Actively engaging (3 pts) | Special notes | Bonus point | Scores | 建物用途名 | [8 empty] | 評価 対象 判定 |  | 建物全体 | 住居宿泊 | CASBEE 評価結果 | CASBEE 評価素点 | 素点 対象外or 1～3点 |  | 加点 チェック 判定 | 小項目別 点数 | 大項目別 点数
| Major item |  | Minor item | [10 empty] | 事 | 学 | 物 | 飲 | 会 | 工 | 病 | ホ | 住 |  | 1～3点 | 1 | 0 | 1～5点 | 1～3点
Goal 1. No Poverty | Assessment based on Goal 12: Responsible Consumption and Production, etc.
Goal 2. Zero Hunger | Assessment based on Goal 12: Responsible Consumption and Production, etc.
Goal 3. Good Health and Well-Being | 3.1 | Thermal environment | 3.1.1 | Ensure a comfortable room temperature | The air conditioning system is designed to provide a comfortable room temperature even during peak load periods. | All | Q1.2.1.1 "Room temperature" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
|  |  | 3.1.2 | Improving thermal insulation | Efforts are being made to reduce heat gain or loss from the outside of the building. | All | Q1.2.1.2 "Perimeter performance" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 3.1.3 | Creating a homogeneous thermal environment | (i) Detailed zoning air conditioning is used to eliminate uneven temperatures in the indoor environment and create a comfortable environment. | Non-Sch, Non-Apt | Q1.2.1.3 "Zoned control" |  | ● |  |  |  | 2 | 事務所 |  | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル |  | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
[5 empty] | (ii) A type of air conditioning system is used to reduce the vertical temperature difference and airflow velocity (residual air velocity) in the occupied area. | All | Q1.2.3 "Type of air conditioning system" |  | ● |  |  |  |  | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2
| 3.2 | Air and sanitation | 3.2.1 | Use appropriate ventilation measures | Efforts are being made to exceed ventilation levels required by the building code, the built environment sanitation code, and school environmental sanitation standards to improve air quality. | All | Q1.4.2 "Ventilation" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
|  |  | 3.2.2 | Ensure adequate humidity control | The system is designed to allow humidification and dehumidification for comfort and health reasons. | All | Q1.2.2 "Humidity control" | [5 empty] | N.A. | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | N.A. |  | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | FALSE | #DIV/0!
|  |  | 3.2.3 | Take measures to address indoor air quality | Adequate measures are taken to avoid air quality pollution by chemical pollutants. | All | Q1.4.1.1 "Chemical pollutant " |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 3.2.4 | Prevent passive smoking | Measures are taken to prevent non-smokers from being exposed to smoke, such as non-smoking or installation of smoking booths. | Non-Apt | Q1.4.3.2 "Control of smoking" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル |  | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 3.2.5 | Keep sink and basin areas sanitary | The rooms are easy to clean, including the water areas, and are made of stain-resistant materials, etc. Maintenance is taken into consideration. | All | Q2.1.3.2 "Securing maintenance functions" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
| 3.3 | Lighting and illumination | 3.3.1 | Use daylight to ensure adequate brightness | The building is equipped with daylight devices as well as windows on the exterior walls of the building. | All | Q1.3.1.3 "Daylight devices" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
|  |  | 3.3.2 | Reduce glare on window surfaces | Efforts are being made for anti-glare measures on window surfaces (e.g., blinds, curtains, eaves, etc.). | Non-Rtl, non-Rst, Non-Hal | Q1.3.2.1 "Daylight control" |  | ● |  |  |  | 2 | 事務所 | 学校 |  |  |  | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 3.3.3 | Provide adequate lighting | Lighting control in the subject space is assessed, such as detailed lighting control and automatic control. | Non-Rst | Q1.3.4 "Lighting controllability" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 |  | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
| 3.4 | Sound environment | 3.4.1 | Ensure sound insulation and sound absorption performance | Efforts are being made to use building materials with high sound insulation and sound absorption performance for window sashes, walls, and floors as a means of ensuring quietness within the space. | All | Q1.1 "Sound environment" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
| 3.5 | Creating a safe environment | 3.5.1 | Implement building security measures | Not engaging in any of the following efforts (no applicable efforts), Engaging in one applicable effort, Actively engaging in two or more applicable efforts; 1) Security cameras and motion sensors are installed. 2) An access control system is in place. 3) Subscribed to a 24-hour security service. 4) A security staff is stationed in the building. | All | SDGs original | [5 empty] | #DIV/0! | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | FALSE |  |  |  |  | 0 | #DIV/0! | FALSE | #DIV/0! | 3
| 3.6 | Creating a secure environment | 3.6.1 | Implement barrier-free measures | The building is designed to allow all people to use the building without any inconvenience, while meeting the standards for facilitating the movement of people in the building. | All | Q2.1.1.3 "Barrier-free planning" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
| 3.7 | Environment with consideration for prevention of nosocomial infections | 3.7.1 | Apply nosocomial infection control measures | Not engaging in any of the following efforts (no applicable efforts), Actively engaging in one or more applicable efforts; Each room is planned to meet the ventilation requirements (room pressure, ventilation frequency, and final filter efficiency) corresponding to the cleanliness class of the "Guideline for Design and Management of Hospital HVAC systems HEAS-02-2013" of the Japan Association of Healthcare Equipment and Services. | Hsp | SDGs original | [5 empty] | N.A. | [9 empty] | N.A. | FALSE |  |  |  |  | #DIV/0! | #DIV/0! | FALSE | #DIV/0! | #DIV/0! | bar: 病院 病院 病院
| 3.8 | Consideration for the surrounding environment | 3.8.1 | Reduce noise, vibration, and odors | (i) The device is significantly lower than the current regulatory standards stipulated in the Noise Regulation Law or the Large-Scale Retail Stores Location Law, local ordinances, etc. | All | LR3.3.1.1 "Noise" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
[5 empty] | (ii) The device is significantly lower than the current regulatory standards set forth in the Vibration Regulation Law and local ordinances. | All | LR3.3.1.2 "Vibration |  | ● |  |  |  |  | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2
[5 empty] | (iii) Devices that meet the permissible limit values for the concentration of specific odor substances specified in the Odor Control Law, local ordinances, etc. | All | LR3.3.1.3 "Odor" |  | ● |  |  |  |  | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2
|  |  | 3.8.2 | Reduce wind damage and sunlight obstruction | (i) Restrictions of wind damage. | All | LR3.3.2.1 "Restriction of wind damage" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
[5 empty] | (ii) Restriction of sunlight obstruction. | All | LR3.3.2.3 "Restriction of sunlight obstruction" |  | ● |  |  |  |  | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2
|  |  | 3.8.3 | Reduce light pollution | Efforts are being made on anti-glare measures against outdoor lighting and indoor lighting that leaks light outside. | All | LR3.3.3 "Light Pollution" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 3.8.4 | Reduce thermal effects on surroundings | Efforts are being made to contribute to the reduction of off-site heat load, such as measures to reduce the heat island effect. | All | LR3.2.2 "Heat Island Effect" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 3.8.5 | Reduce chemical dispersal to surrounding areas | Efforts are being made to reduce the use of chemical substances that may have an impact on the environment. | All | LR2.3.1 "Use of materials without harmful substances" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
Goal 4. Quality Education | 4.1 | Design that allow floor plans, etc. to be changed to meet the needs of residents | 4.1.1 | Prepare a study space in the home | Not engaging in any of the following efforts (no applicable efforts), Engaging in one applicable effort, Actively engaging in two or more applicable efforts; 1) In apartments, there is a separate study space. 2) In apartments, study spaces/study corners are located in common spaces. 3) In apartments, there is an ingenious study space that can be used in accordance with the changing stages of the family. 4) There is a study space/study corner in the common area of the apartments. | Apt | SDGs original | [5 empty] | N.A. | [8 empty] | 集合住宅 | N.A. | FALSE |  |  |  |  | #DIV/0! | #DIV/0! | FALSE | #DIV/0! | #DIV/0!
| 4.2 | Creating a thermal, air, light, and sound environment suitable for learning | 4.2.1 | Ensure a comfortable room temperature | The air conditioning system is designed to provide a comfortable room temperature even during peak load periods. | All | Q1.2.1.1 "Room temperature" |  | ● |  | （The result for 3.1.1 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
|  |  | 4.2.2 | Improving thermal insulation | Efforts are being made to reduce heat gain or loss from the outside of the building. | All | Q1.2.1.2 "Perimeter performance" |  | ● |  | （The result for 3.1.2 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 4.2.3 | Use daylight to ensure adequate brightness | The building is equipped with daylight devices as well as windows on the exterior walls of the building. | All | Q1.3.1.3 "Daylight devices" |  | ● |  | （The result for 3.3.1 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 4.2.4 | Use appropriate ventilation measures | Efforts are being made to exceed ventilation levels required by the building code, the built environment sanitation code, and school environmental sanitation standards to improve air quality. | All | Q1.4.2 "Ventilation" |  | ● |  | （The result for 3.2.1 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 4.2.5 | Take measures to address indoor air quality | Adequate measures are taken to avoid air quality pollution by chemical pollutants. | All | Q1.4.1.1 "Chemical pollutant contents" |  | ● |  | （The result for 3.2.3 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 4.2.6 | Ensure sound insulation and sound absorption performance | Efforts are being made to use building materials with high sound insulation and sound absorption performance for window sashes, walls, and floors as a means of ensuring quietness within the space. | All | Q1.1 "Sound environment" |  | ● |  | （The result for 3.4.1 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
| 4.3 | Creating a learning environment | 4.3.1 | Arrange learning spaces in schools | Not engaging in any of the following efforts (no applicable efforts), Actively engaging in one or more applicable efforts; 1) Establishment of study rooms 2) Secure space for active learning | Sch | SDGs original | [5 empty] | N.A. | [9 empty] | N.A. | FALSE |  |  |  |  | #DIV/0! | #DIV/0! | FALSE | #DIV/0! | #DIV/0! | bar: 学校 学校 学校 学校 学校 学校
|  |  | 4.3.2 | Prepare the necessary facilities for learning | Not engaging in any of the following efforts (no applicable efforts), Engaging in one applicable effort, Actively engaging in two or more applicable efforts; 1) Meet the standards (minimum level) for facilitating mobility in buildings under the new Barrier-Free Japan Act. (Q2.1.1.3 Level 4 or higher) 2) An environment in which students can use ICT one by one according to class development has been established through the provision of movable computers, etc. and wireless LAN. 3) Built environment and facilities that contribute to environmental education (new energy, energy conservation, natural energy utilization, wood utilization, resource recycling, etc.) are in place. 4) Other than 3), buildings and facilities conducive to SDG education are in place. | Sch | SDGs original | [5 empty] | N.A. | [9 empty] | N.A. | FALSE |  |  |  |  | #DIV/0! | #DIV/0! | FALSE | #DIV/0! | bar: 学校 学校 学校 学校 学校 学校
| 4.4 | Universal design | 4.4.1 | Create an environment of education for all | Not engaging in any of the following efforts (no applicable efforts), Actively engaging in one or more applicable efforts; 1) Compliance with the minimum level of the New Barrier-Free Building Act (Level 4 or higher in Q2.1.1.3 of CASBEE-BD/NC) 2) Installation of LGBT-friendly restrooms | Sch | SDGs original | [5 empty] | N.A. | [9 empty] | N.A. | FALSE |  |  |  |  | #DIV/0! | #DIV/0! | FALSE | #DIV/0! | #DIV/0! | bar: 学校 学校 学校 学校 学校 学校
Goal 5. Gender Equality | 5.1 | Spatial margin | 5.1.1 | Create spatial margins | The building has a degree of freedom in terms of floor height and space shape, taking into consideration the possibility of future changes in use. | Non-Hal | Q2.3.1 "Spatial margin" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 |  | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
| 5.2 | Design that reduce the burden of housework, child-rearing, nursing care, etc. | 5.2.1 | Reduce the burden of housework, child care, nursing care, etc. | Not engaging in any of the following efforts (no applicable efforts), Engaging in one applicable effort, Actively engaging in two or more applicable efforts; 1) The design is designed to reduce the burden of housework. 2) The design is designed to reduce the burden of childcare.3) The design is designed to reduce the burden of care. | Apt | SDGs original | [5 empty] | N.A. | [8 empty] | 集合住宅 | N.A. | FALSE |  |  |  |  | #DIV/0! | #DIV/0! | FALSE | #DIV/0! | #DIV/0!
|  |  | 5.2.2 | Implement barrier-free measures | The building is designed to allow all people to use the building without any inconvenience, in compliance with the standards for facilitating building movement. | All | Q2.1.1.3 "Barrier-free planning" |  | ● |  | （The result for 3.6.1 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
| 5.3 | Design that accommodate different temperature/cooling sensation evaluations by gender | 5.3.1 | Control air conditioning according to the individual | Not engaging in any of the following efforts (no applicable efforts), Actively engaging in one or more applicable efforts; Installation of personal air conditioning or other equipment that enables individual adjustment of temperature and cooling | Off | SDGs original | [5 empty] | 3 | 事務所: 事務所 |  | 対象 | FALSE |  |  |  |  | 0 | 3 | FALSE | 3 | 3
| 5.4 | Designing for LGBT and other groups | 5.4.1 | Designing with LGBT considerations | Not engaging in any of the following efforts (no applicable efforts), Actively engaging in one or more applicable efforts; 1) Installation of LGBT-friendly restrooms 2) Other LGBT-friendly design innovations | All | SDGs original | [5 empty] | #DIV/0! | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | FALSE |  |  |  |  | 0 | #DIV/0! | FALSE | #DIV/0! | 1
Goal 6. Clean Water and Sanitation | 6.1 | Water saving | 6.1.1 | Adopt water saving devices | Water saving systems are being introduced. | All | LR2.1.1 "Water Saving" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
| 6.2 | Use of rain water and grey water | 6.2.1 | Use of rain water and waste water | Efforts are being made to use rain water and grey water. | All | LR2.1.2 "Rain water & waste water use" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
| 6.3 | Rain water infiltration | 6.3.1 | Work to infiltrate rain water | Measures are implemented to prevent rain water from infiltrating into the ground. | All | LR3.2.3.1 "Reduction of rain water discharge loads" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 1.5
|  |  | 6.3.2 | Consider for groundwater systems | Not engaging in any of the following efforts (no applicable efforts), Actively engaging in one or more applicable efforts; 1) Devices to reduce obstruction to groundwater flow 2) Active on-site greening | All | SDGs original | [5 empty] | 1 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | FALSE |  |  |  |  | 0 | 1 | FALSE | 1
| 6.4 | Soil contamination countermeasures | 6.4.1 | Preventing soil contamination | Not engaging in any of the following efforts (no applicable efforts), Actively engaging in one or more applicable efforts; 1) Conduct soil contamination survey 2) Excavation and removal of contaminated soil | All | SDGs original | [5 empty] | 1 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | FALSE |  |  |  |  | 0 | 1 | FALSE | 1 | 1
| 6.5 | Sewage purification | 6.5.1 | Properly dispose of sewage | Efforts are being made to devise a method that is significantly lower than the emission standards set by the Water Pollution Control Law, the Sewerage Law, and regional public organizations. | All | LR3.2.3.2 "Sewage load suppression" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
| 6.6 | Design that keep sink and basin areas sanitary | 6.6.1 | Keep sink and basin areas sanitary | The rooms are easy to clean, including the water areas, and are made of stain-resistant materials, etc. Maintenance is taken into consideration. | All | Q2.1.3.2 "Securing maintenance functions" |  | ● |  | （The result for 3.2.5 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
| 6.7 | Ensure reliability of water supply and drainage systems | 6.7.1 | Conduct periodic inspections of water supply and drainage systems | Efforts are being made to improve the reliability of water supply & drainage and sanitation facilities. | All | Q2.2.4.2 "Water supply & drainage |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
Goal 7. Affordable and Clean Energy | 7.1 | Design that contribute to energy conservation | 7.1.1 | Work to reduce heat load | The company is taking measures to reduce heat load, which contributes to the reduction of energy used for heating and cooling. | All | LR1.1 "Control of heat load on the building envelopes" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2.3333
|  |  | 7.1.2 | Engage in direct natural energy utilization | Efforts are being made to install equipment and systems that enable direct natural energy utilization and other design innovations. | All | LR1.2 "Natural Energy Utilization (Direct Use)" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 7.1.3 | Adopt equipment and systems with high energy-saving performance | Efforts are being made to install equipment and systems that can significantly reduce energy consumption. | All | LR1.3 "Efficiency in building service system" |  |  | ● |  |  | 3 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 5 | 0 | 5 | 3 | 3 | 3 | FALSE | 3
| 7.2 | Design that contribute to energy creation | 7.2.1 | Engage in energy creation | Not engaging in any of the following efforts (no applicable efforts), Engaging in one applicable effort, Actively engaging in two or more applicable efforts; 1) Solar heat utilization (hot water utilization), etc. 2) Solar power use (electricity use), etc. 3) Unused heat utilization (geothermal heat utilization/well water utilization/river water utilization heat pumps), etc. 4) Others (biomass, other renewable energy on-site) 5) Off-site renewable energy (award only renewables evaluated in LR1.3 "Efficiency in building service system") | All | SDGs original | [5 empty] | #DIV/0! | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | FALSE |  |  |  |  | 0 | #DIV/0! | FALSE | #DIV/0! | 2
| 7.3 | Design that contribute to energy storage | 7.3.1 | Engage in energy storage | Equipment and systems related to energy storage that promote the use of renewable energy have been introduced. | All | LR1.4.3 "Expanding adoption of non-fossil energy" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
| 7.4 | Linkage with distributed energy systems | 7.4.1 | Work with distributed energy systems in the community | Not engaging in any of the following efforts (no applicable efforts), Engaging in one applicable effort, Actively engaging in two or more applicable efforts; 1) Existence or non-existence of initiatives for area use (building groups/supply-demand linkage) 2) Provision of emergency power supply to the community (BCP compliance is also subject to assessment) 3) Introduction of CEMS 4) Active use of renewable energy/unused heat | All | SDGs original | [5 empty] | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | FALSE |  |  |  |  | 2 | 2 | FALSE | 2 | 2
| 7.5 | Installation of energy management systems | 7.5.1 | Managing energy | Monitoring is implemented and HEMS or BEMS for efficient operation of energy is installed. | All | LR1.4.1 "Monitoring" and LR1.4.2 "Operation & Management System" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
| 7.6 | LCP, BCP, and emergency energy | 7.6.1 | Securing energy in an emergency | Efforts are being made to secure power supply in case of emergency, such as power failure. (e.g., Facility equipped with emergency power generation equipment and uninterruptible power supply equipment, or facility avoiding installation in underground spaces) | All | Q2.2.4.3 "Electrical equipment" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
| 7.7 | Efforts toward ZEH and ZEB | 7.7.1 | Work on ZEH and ZEB conversion | Not engaging in any of the following efforts (no applicable efforts), Actively engaging in one or more applicable efforts; ZEH Ready, ZEB Ready or higher | All | SDGs original | [5 empty] | 1 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | 1 |  |  |  |  | 1 | 1 | FALSE | 1 | 1
| 7.8 | Efforts toward LCCM, energy consumption and continuous efforts towards GHG emission reduction | 7.8.1 | Working toward carbon neutrality | Efforts are being made to reduce the WLC of buildings. | All | LR3.1 "Consideration of global warming" | #VALUE! | #VALUE! | #VALUE! |  |  | #VALUE! | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | #VALUE! |  | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | FALSE | #VALUE! | #VALUE!
Goal 8. Decent Work and Economic Growth | 8.1 | Design to create an environment that enhances intellectual productivity | 8.1.1 | Create a place for intellectual productivity | Not engaging in any of the following efforts (no applicable efforts), Engaging in one applicable effort, Actively engaging in two or more applicable efforts; 1) Availability of spaces that are easy to concentrate, planned and maintained with a view to enhancing intellectual productivity 2) Availability of informal communication spaces that are planned and maintained with a view to enhancing intellectual productivity. 3) Availability of spaces for refreshment and relaxation planned and maintained with a view to enhancing intellectual productivity. | Off | SDGs original | [5 empty] | 3 | 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所: 事務所 |  | 対象 | FALSE |  |  |  |  | 0 | 3 | FALSE | 3 | 3
| 8.2 | Consideration for the health, comfort, and safety of building users | 8.2.1 | Ensure a comfortable room temperature | The air conditioning system is designed to provide a comfortable room temperature even during peak load periods. | All | Q1.2.1.1 "Room temperature" |  | ● |  | （The result for 3.1.1 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
|  |  | 8.2.2 | Improving thermal insulation | Efforts are being made to reduce heat gain or loss from the outside of the building. | All | Q1.2.1.2 "Perimeter performance" |  | ● |  | （The result for 3.1.2 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 8.2.3 | Use daylight to ensure adequate brightness | The building is equipped with daylight devices as well as windows on the exterior walls of the building. | All | Q1.3.1.3 "Daylight devices" |  | ● |  | （The result for 3.3.1 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 8.2.4 | Use appropriate ventilation measures | Efforts are being made to exceed ventilation levels required by the building code, the built environment sanitation code, and school environmental sanitation standards to improve air quality. | All | Q1.4.2 "Ventilation" |  | ● |  | （The result for 3.2.1 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 8.2.5 | Take measures to address indoor air quality | Adequate measures are taken to avoid air quality pollution by chemical pollutants. | All | Q1.4.1.1 "Chemical pollutant contents" |  | ● |  | （The result for 3.2.3 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 8.2.6 | Ensure sound insulation and sound absorption performance | Efforts are being made to use building materials with high sound insulation and sound absorption performance for window sashes, walls, and floors as a means of ensuring quietness within the space. | All | Q1.1 "Sound environment" |  | ● |  | （The result for 3.4.1 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
| 8.3 | Measures to reduce the amount of waste generated at each stage of the production and disposal of housing and building | 8.3.1 | Reduce material usage | Efforts are being made to use high-strength materials and measures to reduce the amount of material used. | All | LR2.2.1 "Reducing use of materials" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
|  |  | 8.3.2 | Continued use of building frame, etc. | The existing structural frame is reused. | All | LR2.2.2 "Continuing use of existing structural frame, etc." |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 8.3.3 | Use recycled materials in building frame materials | Recycled materials are used in major structural components. | All | LR2.2.3 "Use of recycled materials as structural materials" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 8.3.4 | Use recycled materials other than building frame materials | Recycled materials are used in areas other than the building frame. | All | LR2.2.4 "Use of recycled materials as non-structural materials" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 8.3.5 | Use timber from sustainable forestry | Timber from sustainable forestry is used. | All | LR2.2.5 "Timber from sustainable forestry" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 8.3.6 | Work to enhance the reusability of components and materials | Measures to promote recycling at the time of dismantling and disposal, such as ease of sorting, are taken. | All | LR2.2.6 "Reusability of components and materials" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
| 8.4 | Innovations for extending the service life of houses and buildings | 8.4.1 | Longer use of frame materials | Necessary measures are taken to extend the period of time before major renovation work is required. | All | Q2.2.2.1 "Service life of structural materials" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
|  |  | 8.4.2 | Use exterior finish materials longer | Efforts are being made to lengthen the required intervals for repair of exterior wall finish materials. | All | Q2.2.2.2 "Necessary Refurbishment interval for exterior finishes" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 8.4.3 | Use interior finish materials longer | The necessary renewal interval for main interior finishes is being extended. | All | Q2.2.2.3 "Necessary renewal interval for main interior finishes" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 8.4.4 | Use air conditioning and ventilation ducts longer | Necessary replacement intervals for air conditioning and ventilation ducts are being extended. | All | Q2.2.2.4 "Necessary renewal interval for air conditioning and ventilation ducts" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 8.4.5 | Use air conditioning and plumbing piping longer | Necessary renewal intervals for water supply and drainage pipes, and that for HVAC are being extended. | All | Q2.2.2.5 "Necessary renewal interval for HVAC and water supply and drainage pipes" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 8.4.6 | Use major equipment longer | Necessary renewal intervals for major equipment and services are being extended. | All | Q2.2.2.6 "Necessary replacement interval for major equipment and services" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 8.4.7 | Design to withstand natural disasters | Not engaging in any of the following efforts (no applicable efforts), Actively engaging in one or more applicable efforts; 1) Confirm the hazard of the site using hazard maps, etc. 2) Other initiatives to improve resilience to natural disasters | All | SDGs original | [5 empty] | #DIV/0! | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | FALSE |  |  |  |  | 0 | #DIV/0! | FALSE | #DIV/0!
|  |  | 8.4.8 | Improve fire protection performance | Not engaging in any of the following efforts (no applicable efforts), Actively engaging in one or more applicable efforts; Advanced efforts to withstand fire | All | SDGs original | [5 empty] | #DIV/0! | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | FALSE |  |  |  |  | 0 | #DIV/0! | FALSE | #DIV/0!
| 8.5 | Active use of local timber | 8.5.1 | Engage in the use of local resources | The use of materials with local characteristics (for structural materials, interior materials, exterior materials, exterior construction, etc.) is being considered. | All | Q3.3.1 "Attention to local characteristics & improvement of comfort - I 2) Use of materials with local characteristics" and Q3.2 "Attention to townscape and landscape 4) Formation of a good landscape with materials with local characteristics" | ● |  |  |  |  | 1 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 1 |  | 1 | 1 | 1 | 1 | FALSE | 1 | 1
Goal 9. Industry, Innovation and Infra- structure | 9.1 | Foster momentum for new technology development through active use of state-of-the-art technology and building materials on site | 9.1.1 | Adopt the latest technology | Not engaging in any of the following efforts (no applicable efforts), Engaging in one applicable effort, Actively engaging in two or more applicable efforts; 1) Adoption of bldg. materials using the latest tech. (retroreflective solar reflective film, etc.) 2) Adoption of equipment using the latest technology (e.g., IoT for equipment) 3) Adoption of systems using the latest tech. (e.g., lifecycle management system using BIM) 4) Others (utilization of AI, etc.) | All | SDGs original | [5 empty] | #DIV/0! | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | FALSE |  |  |  |  | 0 | #DIV/0! | FALSE | #DIV/0! | 1
|  |  | 9.1.2 | Work to make buildings smarter | Not engaging in any of the following efforts (no applicable efforts), Engaging in one applicable effort, Actively engaging in two or more applicable efforts; 1) Introduction of high-speed, high-capacity, low-latency information systems, including 5G support 2) Optimal operation of facilities based on analysis of HEMS / BEMS data using AI 3) Cooperation with CEMS | All | SDGs original | [5 empty] | #DIV/0! | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | FALSE |  |  |  |  | 0 | #DIV/0! | FALSE | #DIV/0!
| 9.2 | Creating communication, relaxation, refreshment space, etc. | 9.2.1 | Create space for refreshment | Spaces for refreshment and other amenities necessary for a comfortable office life are devised. | Off, Rtl, Fct | Q2.1.2.2 "Space for refreshment" |  | ● |  |  |  | 2 | 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所: 事務所; 事務所 物販店 物販店 物販店 物販店 物販店 物販店 物販店 物販店 物販店 物販店 物販店 物販店 物販店 物販店 物販店 物販店 物販店 物販店 物販店 物販店 物販店 物販店 物販店: 物販店; 事務所 工場 工場 工場 工場 工場 工場 工場 工場 工場 工場 工場 工場 工場 工場 工場 工場 工場 工場 工場 工場 工場 工場 工場: 工場 |  | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2.5
|  |  | 9.2.2 | Create space for communication | Not engaging in any of the following efforts (no applicable efforts), Actively engaging in one or more applicable efforts; 1) Availability of formal communication spaces that are planned and maintained with a view to enhancing intellectual productivity. 2) Availability of informal communication spaces that are planned and maintained with a view to enhancing intellectual productivity. | Off | SDGs original | [5 empty] | 3 | 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所: 事務所 |  | 対象 | 3 |  |  |  |  | 3 | 3 | FALSE | 3
| 9.3 | Access to information and communication technology | 9.3.1 | Adopt advanced communication technologies | Comfortable communication environment facilities are installed. | Off, Fct, Htl, Apt | Q2.1.1.2 "use of advanced information & IT equipment" |  | ● |  |  |  | 2 | 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所 事務所: 事務所; 事務所 工場 工場 工場 工場 工場 工場 工場 工場 工場 工場 工場 工場 工場 工場 工場 工場 工場 工場 工場 工場 工場 工場 工場: 工場; 事務所 ホテル ホテル ホテル ホテル ホテル ホテル ホテル ホテル ホテル ホテル ホテル ホテル ホテル ホテル ホテル ホテル ホテル ホテル ホテル ホテル ホテル ホテル ホテル: ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
| 9.4 | Introduction to resilient design | 9.4.1 | Protecting internal equipment | Measures to protect its internal facilities are taken. | All | Q2.2.1.1 "Earthquake-resistance (resistance to building breakage)" and Q2.2.1.2 "Seismic isolation, seismic & vibration control (internal equipment protection)" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
|  |  | 9.4.2 | Ensure resilience of HVAC system | Efforts are being made to improve the reliability of the HVAC system. | All | Q2.2.4.1 "HVAC system" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 9.4.3 | Ensure resilience of water supply & drainage and sanitation systems | Efforts are being made to improve the reliability of water supply & drainage and sanitation facilities. | All | Q2.2.4.2 "Water supply & drainage, sanitation" |  | ● |  | （The result for 6.7.1 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 9.4.4 | Ensure resilience of electrical equipment | Efforts are being made to secure power supply in case of emergency, such as power failure. (e.g., The facility equipped with emergency power generation equipment and uninterruptible power supply equipment, or the facility avoiding installation in underground spaces) | All | Q2.2.4.3 "Electrical equipment" |  | ● |  | （The result for 7.6.1 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 9.4.5 | Ensure resilience of support method of machines & ducts | Efforts are being made to improve the reliability of mechanical and piping supports. | All | Q2.2.4.4 "Support method of machines & ducts" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 9.4.6 | Ensure resilience of communication wiring | Efforts are being made to improve the reliability of communications & IT equipment. | All | Q2.2.4.5 "Communications & IT equipment" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
| 9.5 | Identification of site hazards | 9.5.1 | Identify site hazards and share information | Not engaging in any of the following efforts (no applicable efforts), Actively engaging in one or more applicable efforts;1) Confirm the hazard of the site using hazard maps, etc.2) Share and disseminate information on disasters using digital signage, etc. | All | SDGs original | [5 empty] | #DIV/0! | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | FALSE |  |  |  |  | 0 | #DIV/0! | FALSE | #DIV/0! | 1
| 9.6 | Ensure performance to withstand earthquake, fire, wind, flood, etc. | 9.6.1 | Adopt the latest technology for disaster prevention | Not engaging in any of the following efforts (no applicable efforts), Engaging in one applicable effort, Actively engaging in two or more applicable efforts; 1) Devices against earthquakes (latest seismic isolation, vibration control (damping), etc.) 2) Devices against fire (e.g., use of the latest noncombustible materials) 3) Innovations against wind and flood damage (use of designs that minimize wind and flood damage using CFD technology) 4) Other innovations related to disasters | All | SDGs original | [5 empty] | #DIV/0! | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | FALSE |  |  |  |  | 0 | #DIV/0! | FALSE | #DIV/0! | 2
Goal 10. Reduced Inequalities | Assessment based on Goal 5: Gender Equality, etc.
Goal 11. Sustainable Cities and Communities | 11.1 | Low cost through rational design and construction while ensuring environmental performance | 11.1.1 | Ensure basic environmental performance of the building | (i) Building materials with high sound insulation performance are used for window sashes, walls, and floors as a measure to prevent sound in the space from leaking to the outside. | All | Q1.1 "Sound environment" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2.5
[5 empty] | (ii) The air conditioning system is designed to provide a comfortable room temperature even during peak load periods. | All | Q1.2.1.1 "Room temperature" |  | ● |  |  |  |  | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2
[5 empty] | (iii) Measures are taken to prevent heat from entering or escaping from outside the room. | All | Q1.2.1.2 "Perimeter performance" |  | ● |  |  |  |  | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2
[5 empty] | (iv) The building is equipped with daylight devices as well as windows on the exterior walls of the building to actively utilize daylight. | All | Q1.3.1.3 "Daylight devices" |  | ● |  |  |  |  | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2
[5 empty] | (v) Adequate measures are taken to avoid air quality pollution by chemical pollutants. | All | Q1.4.1.1 "Chemical pollutant " |  | ● |  |  |  |  | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2
[5 empty] | (vi) Efforts are made to exceed the ventilation levels of the building code, the building sanitation code, and the school environmental sanitation standards to improve air quality. | All | Q1.4.2 "Ventilation" |  | ● |  |  |  |  | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2
|  |  | 11.1.2 | Reduce running costs while ensuring basic environmental performance | Not engaging in any of the following efforts (no applicable efforts), Engaging in one applicable effort, Actively engaging in two or more applicable efforts; 1) Efforts to reduce costs during construction 2) Efforts to reduce costs during operation 3) Efforts to reduce costs at the time of repair and renewal | All | SDGs original | [5 empty] | #DIV/0! | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | FALSE |  |  |  |  | 0 | #DIV/0! | FALSE | #DIV/0!
| 11.2 | Prevention of traffic accidents, coordination with public transportation | 11.2.1 | Reduce traffic and accidents due to automobile use | Efforts are being made to encourage building users to use means of transportation other than automobiles, to secure appropriate parking spaces, and to ensure the safety of parking lot entrances and exits. | All | LR3.2.3.3 "Traffic load control" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
| 11.3 | Public Involvement | 11.3.1 | Encourage community participation | Efforts are being made to encourage the participation of local residents in the operation and management of the building. | All | Q3.3.1 "Attention to local characteristics & improvement of comfort - V. Involvement of building users, etc." | ● |  |  |  |  | 1 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 1 |  | 1 | 1 | 1 | 1 | FALSE | 1 | 1
| 11.4 | Reduction of environmental load on the surrounding environment | 11.4.1 | Contribute to the prevention of air pollution | Efforts are being made to significantly lower its contaminants from the emission than the standards set by Air Pollution Control Law, recommended guidelines for low NOx small-scale combustion equipment, or by local ordinances, etc. | All | LR3.2.1 "Prevention of air pollution" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 1.75
|  |  | 11.4.2 | Properly dispose of sewage | Efforts are being made to significantly lower its contaminants from the discharge than the standards set by the Water Pollution Control Law, the Sewerage Law, and regional public organizations. | All | LR3.2.3.2 "Sewage load suppression" |  | ● |  | （The result for 6.5.1 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 11.4.3 | Control rain water runoff | Runoff control measures, such as primary storage of rain water and underground infiltration, are in place. | All | LR3.2.3.1 "Reduction of rain water discharge loads" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 11.4.4 | Preventing soil contamination | Not engaging in any of the following efforts (no applicable efforts), Actively engaging in one or more applicable efforts; 1) Conduct soil contamination survey 2) Excavation and removal of contaminated soil | All | SDGs original | ● |  |  | （The result for 6.4.1 is transferred.） |  | 1 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | 1 |  |  |  |  | 1 | 1 | FALSE | 1
| 11.5 | Introduction to resilient design | 11.5.1 | Protecting internal equipment | Measures are taken to protect its internal facilities. | All | Q2.2.1.1 "Earthquake-resistance (resistance to building breakage)" and Q2.2.1.2 "Seismic isolation, seismic & vibration control (internal equipment protection)" |  | ● |  | （The result for 9.4.1 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
|  |  | 11.5.2 | Ensure resilience of HVAC system | Efforts are being made to improve the reliability of the HVAC system. | All | Q2.2.4.1 "HVAC system" |  | ● |  | （The result for 9.4.2 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 11.5.3 | Ensure resilience of water supply & drainage and sanitation systems | Efforts are being made to improve the reliability of water supply & drainage and sanitation facilities. | All | Q2.2.4.2 "Water supply & drainage, sanitation" |  | ● |  | （The result for 6.7.1 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 11.5.4 | Ensure resilience of electrical equipment | Efforts are being made to secure power supply in case of emergency, such as power failure. (e.g., The facility equipped with emergency power generation equipment and uninterruptible power supply equipment, or the facility avoiding installation in underground spaces) | All | Q2.2.4.3 "Electrical equipment" |  | ● |  | （The result for 7.6.1 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 11.5.5 | Ensure resilience of support method of machines & ducts | Efforts are being made to improve the reliability of mechanical and piping supports. | All | Q2.2.4.4 "Support method of machines & ducts" |  | ● |  | （The result for 9.4.5 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 11.5.6 | Ensure resilience of communication wiring | Efforts are being made to improve the reliability of communications & IT equipment. | All | Q2.2.4.5 "Communications & IT equipment" |  | ● |  | （The result for 9.4.6 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
| 11.6 | Identification of site hazards | 11.6.1 | Identify site hazards and share information | Not engaging in any of the following efforts (no applicable efforts), Actively engaging in one or more applicable efforts; 1) Confirm the hazard of the site using hazard maps, etc. 2) Share and disseminate information on disasters using digital signage, etc. | All | SDGs original | ● |  |  | （The result for 9.5.1 is transferred.） |  | 1 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | 1 |  |  |  |  | 1 | 1 | FALSE | 1 | 1
| 11.7 | Site security measures | 11.7.1 | Provide security measures for the site and outbuildings | Crime prevention measures are being taken at the site and exterior to improve security performance. | All | Q3.3.1 "Attention to local characteristics & improvement of comfort - IV Consideration of crime prevention" | ● |  |  |  |  | 1 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 1 |  | 1 | 1 | 1 | 1 | FALSE | 1 | 1
| 11.8 | Townscape and landscape-friendly architectural planning | 11.8.1 | Create a favorable townscape and landscape | Efforts are being made to improve the townscape and landscape of the surrounding area (e.g., use of materials suited to the characteristics of the area, creation of a favorable landscape through planting, etc.). | All | Q3.2 "Consideration for townscape and landscape" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
| 11.9 | Consideration for biodiversity, planning of exterior structures with consideration for ecosystem preservation | 11.9.1 | Protecting the biological environment | Initiatives that contribute to the preservation and creation of biotope are involved. | All | Q3.1 "Preservation and creation of biotope" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
| 11.10 | Consideration for the surrounding environment | 11.10.1 | Reduce noise, vibration, and odors | (i) It is devised to be significantly lower than the current regulatory standards stipulated in the Noise Regulation Law or the Large-Scale Retail Stores Location Law, local ordinances, etc. | All | LR3.3.1.1 "Noise" |  | ● |  | （The result for 3.8.1 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
[5 empty] | (ii) It is devised to be significantly lower than the current regulatory standards set forth in the Vibration Regulation Law and local ordinances. | All | LR3.3.1.2 "Vibration |  | ● |  |  |  |  | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2
[5 empty] | (iii) It is devised to meet the permissible limit values for the concentration of specific odor substances specified in the Odor Control Law, local ordinances, etc. | All | LR3.3.1.3 "Odor" |  | ● |  |  |  |  | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2
|  |  | 11.10.2 | Reduce wind damage and sunlight obstruction | (i) Restrictions of wind damage. | All | LR3.3.2.1 "Restriction of wind damage" |  | ● |  | （The result for 3.8.2 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
[5 empty] | (ii) Restriction of sunlight obstruction. | All | LR3.3.2.3 "Restriction of sunlight obstruction" |  | ● |  |  |  |  | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2
|  |  | 11.10.3 | Reducing light pollution | Efforts on anti-glare measures are being made against outdoor lighting and indoor lighting that leaks light outside. | All | LR3.3.3 "Light Pollution" |  | ● |  | （The result for 3.8.3 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 11.10.4 | Reduce thermal effects on surroundings | Efforts are being made to contribute to the reduction of off-site heat load, such as measures to reduce the heat island effect. | All | LR3.2.2 "Heat Island Effect" |  | ● |  | （The result for 3.8.4 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 11.10.5 | Reduce chemical dispersal to surrounding areas | Efforts are being made to reduce the use of chemical substances that may have an impact on the environment. | All | LR2.3.1 "Use of materials without harmful substances" |  | ● |  | （The result for 3.8.5 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
| 11.11 | Creating communication space | 11.11.1 | Provide space and facility functions | Efforts are being made to contribute to the community by providing space and facilities. | All | Q3.3.1 "Attention to local characteristics & improvement of comfort - II Contribution to the local community by providing space & facility functions" |  |  | ● |  |  | 3 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 4 |  | 4 | 3 | 3 | 3 | FALSE | 3 | 3
| 11.12 | Architectural planning linked to smart urbanization | 11.12.1 | Work to make buildings smarter | Not engaging in any of the following efforts (no applicable efforts), Engaging in one applicable effort, Actively engaging in two or more applicable efforts; 1) Introduction of high-speed, high-capacity, low-latency information systems, including 5G support 2) Optimal operation of facilities based on analysis of HEMS / BEMS data using AI 3) Cooperation with CEMS | All | SDGs original | ● |  |  | （The result for 9.1.2 is transferred.） |  | 1 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | 1 |  |  |  |  | 1 | 1 | FALSE | 1 | 1
| 11.13 | Active use of local timber | 11.13.1 | Engage in the use of local resources | The use of materials with local characteristics (for structural materials, interior materials, exterior materials, exterior construction, etc.) is being considered. | All | Q3.3.1 "Attention to local characteristics & improvement of comfort - I 2) Use of materials with local characteristics" and Q3.2 "Attention to townscape and landscape 4) Formation of a good landscape with materials with local characteristics" | ● |  |  | （The result for 8.5.1 is transferred.） |  | 1 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 1 |  | 1 | 1 | 1 | 1 | FALSE | 1 | 1
| 11.14 | Assessment and certification of environmental performance of houses and buildings | 11.14.1 | Utilize labeling and certification for built environment | Not engaging in any of the following efforts (no applicable efforts), Actively engaging in one or more applicable efforts; Proactive use of labeling and certification systems that indicate a built environment(CASBEE tools other than CASBEE-BD/NC, BELS, various performance indicators, etc.) | All | SDGs original | [5 empty] | #DIV/0! | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | FALSE |  |  |  |  | 0 | #DIV/0! | FALSE | #DIV/0! | 3
| 11.15 | Inheritance of local characteristics | 11.15.1 | Inheriting history | The historic built environment and existing natural environment are preserved, restored, and rehabilitated to carry on the local characteristics of the area. | All | Q3.3.1 "Attention to local characteristics & improvement of comfort - I 1) Preservation of historic architectural spaces, etc." and Q3.2 "Attention to townscape and landscape 3) Inheritance of landscape history" |  |  | ● |  |  | 3 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 |  | 3 | 3 | 3 | 3 | FALSE | 3 | 3
Goal 12. Responsible Consumption and Production | 12.1 | Performance and initiatives that contribute to the longevity of housing and buildings | 12.1.1 | Longer use of frame materials | Necessary measures are taken to extend the period of time before major renovation work is required. | All | Q2.2.2.1 "Service life of structural materials" |  | ● |  | （The result for 8.4.1 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
|  |  | 12.1.2 | Use exterior finish materials longer | Efforts are being made to lengthen the required intervals for repair of exterior wall finish materials. | All | Q2.2.2.2 "Necessary refurbishment interval for exterior finishes" |  | ● |  | （The result for 8.4.2 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 12.1.3 | Use interior finish materials longer | The necessary renewal interval for main interior finishes is being extended. | All | Q2.2.2.3 "Necessary renewal interval for main interior finishes" |  | ● |  | （The result for 8.4.3 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 12.1.4 | Use air conditioning and ventilation ducts longer | Efforts are being made to lengthen the necessary replacement interval for air conditioning and ventilation ducts. | All | Q2.2.2.4 "Necessary renewal interval for air conditioning and ventilation ducts" |  | ● |  | （The result for 8.4.4 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 12.1.5 | Use air conditioning and plumbing piping longer | Efforts are being made to extend the necessary renewal interval for water supply and drainage pipes and for HVAC and its water supply and drainage pipes. | All | Q2.2.2.5 "Necessary renewal interval for HVAC and water supply and drainage pipes" |  | ● |  | （The result for 8.4.5 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 12.1.6 | Use major equipment longer | Necessary renewal intervals for major equipment and services are being extended. | All | Q2.2.2.6 "Necessary replacement interval for major equipment and services" |  | ● |  | （The result for 8.4.6 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 12.1.7 | Design to withstand natural disasters | Not engaging in any of the following efforts (no applicable efforts), Actively engaging in one or more applicable efforts; 1) Confirm the hazard of the site using hazard maps, etc. 2) Other initiatives to improve resilience to natural disasters | All | SDGs original | ● |  |  | （The result for 8.4.7 is transferred.） |  | 1 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | 1 |  |  |  |  | 1 | 1 | FALSE | 1
|  |  | 12.1.8 | Improve fire protection performance | Not engaging in any of the following efforts (no applicable efforts), Actively engaging in one or more applicable efforts; Advanced efforts to withstand fire | All | SDGs original |  |  | ● | （The result for 8.4.8 is transferred.） |  | 3 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | 3 |  |  |  |  | 3 | 3 | FALSE | 3
| 12.2 | Sustainable use of resources | 12.2.1 | Procuring timber from sustainable forestry | Timber from sustainable forestry is used. | All | LR2.2.5 "Timber from sustainable forestry" |  | ● |  | （The result for 8.3.5 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2.5
|  |  | 12.2.2 | Engage in the use of local resources | The use of materials with local characteristics (for structural materials, interior materials, exterior materials, exterior construction, etc.) is being considered. | All | Q3.3.1 "Attention to local characteristics & improvement of comfort - I 2) Use of materials with local characteristics" and Q3.2 "Attention to townscape and landscape 4) Formation of a good landscape with materials with local characteristics" |  |  | ● | （The result for 8.5.1 is transferred.） |  | 3 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 5 |  | 5 | 3 | 3 | 3 | FALSE | 3
| 12.3 | Periodic inspection | 12.3.1 | Maintain HVAC piping | Efforts are being made to take into account the renewal and repair of air-conditioning piping. | All | Q2.3.3.1 "Ease of air conditioning duct renewal" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
|  |  | 12.3.2 | Maintain water supply and drainage pipes | Efforts are being made to take into account the renewal and repair of water supply and drainage pipes. | All | Q2.3.3.2 "Ease of water supply and drain pipe renewal" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 12.3.3 | Maintain electrical wiring | Efforts are being made to take into account the renewal and repair of electrical wiring. | All | Q2.3.3.3 "Ease of electrical wiring renewal" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 12.3.4 | Maintain communication wiring | Efforts are being made to take into account the renewal and repair of communication wiring. | All | Q2.3.3.4 "Ease of communications cable renewal" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 12.3.5 | Maintain equipment and facilities | The building is being designed to allow renewal and repair while maintaining building functionality. | All | Q2.3.3.5 "ease of equipment renewal" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 12.3.6 | Allocate backup space | Backup space for installation of backup equipment is provided. | All | Q2.3.3.6 "Provision of backup space" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
| 12.4 | Reduction of waste during production and disposal | 12.4.1 | Properly control materials | Not engaging in any of the following efforts (no applicable efforts), Actively engaging in one or more applicable efforts; 1) Ensure traceability 2) Implementation of quantity control using BIM | All | SDGs original | [5 empty] | #DIV/0! | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | FALSE |  |  |  |  | 0 | #DIV/0! | FALSE | #DIV/0! | 2.1667
|  |  | 12.4.2 | Reduce material usage | High-strength materials are used, and measures are taken to reduce the amount of material used. | All | LR2.2.1 "Reducing use of materials" |  | ● |  | （The result for 8.3.1 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 12.4.3 | Continued use of building frame, etc. | The existing structural frame is reused. | All | LR2.2.2 "Continuing use of existing structural frame, etc." |  | ● |  | （The result for 8.3.2 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 12.4.4 | Use recycled materials in building frame materials | Recycled materials are used in major structural components. | All | LR2.2.3 "Use of recycled materials as structural materials" |  | ● |  | （The result for 8.3.3 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 12.4.5 | Use recycled materials other than building frame materials | Recycled materials are used in areas other than the building frame. | All | LR2.2.4 "Use of recycled materials as non-structural materials" |  | ● |  | （The result for 8.3.4 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 12.4.6 | Work to enhance the reusability of components and materials | Measures are taken to promote recycling at the time of dismantling and disposal, such as ease of sorting. | All | LR2.2.6 "Reusability of components and materials " |  | ● |  | （The result for 8.3.6 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
| 12.5 | Operational GHG emissions reduction, water use reduction, monitoring, energy management | 12.5.1 | Adopt water saving devices | Water saving systems are being introduced. | All | LR2.1.1 "Water Saving" |  | ● |  | （The result for 6.1.1 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
|  |  | 12.5.2 | Control air quality | CO2 concentrations are monitored and controlled to maintain proper air quality. | All | Q1.4.3.1 "Monitoring of CO2 " |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 |  |  |  | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 12.5.3 | Reduce waste generation | Efforts are being made to reduce waste generation, sorting measures, and volume and weight reduction during building operations. | All | LR3.2.3.4 "Reduction of waste treatment loads" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 12.5.4 | Managing energy | Monitoring is implemented and HEMS or BEMS for efficient operation of energy is installed. | All | LR1.4 "Initiatives for Efficient Operation" |  | ● |  | （The result for 7.5.1 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
| 12.6 | Reduce use of materials with harmful substances | 12.6.1 | Properly dispose of sewage | Any method is devised to be significantly lower than the emission standards set by the Water Pollution Control Law, the Sewerage Law, and regional public organizations. | All | LR3.2.3.2 "Sewage load suppression" |  | ● |  | （The result for 6.5.1 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 1.75
|  |  | 12.6.2 | Contribute to the prevention of air pollution | Any method is devised to be significantly lower than the emission standards set by Air Pollution Control Law, recommended guidelines for low NOx small-scale combustion equipment, or local ordinances, etc. | All | LR3.2.1 "Air pollution" |  | ● |  | （The result for 11.4.1 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 12.6.3 | Preventing soil contamination | Not engaging in any of the following efforts (no applicable efforts), Actively engaging in one or more applicable efforts; 1) Conduct soil contamination survey 2) Excavation and removal of contaminated soil | All | SDGs original | ● |  |  | （The result for 6.4.1 is transferred.） |  | 1 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | 1 |  |  |  |  | 1 | 1 | FALSE | 1
|  |  | 12.6.4 | Reduce chemical dispersal to surrounding areas | Efforts are being made to reduce the use of chemical substances that may have an impact on the environment. | All | LR2.3.1 "Use of materials without harmful substances" |  | ● |  | （The result for 3.8.5 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
| 12.7 | Reduce GHG emissions during construction, operation, and disposal | 12.7.1 | Working toward carbon neutrality | Efforts are being made to reduce the WLC of buildings. | All | LR3.1 "Consideration of global warming" | #VALUE! | #VALUE! | #VALUE! | （The result for 7.8.1 is transferred.） |  | #VALUE! | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | #VALUE! |  | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | FALSE | #VALUE! | #VALUE!
| 12.8 | Supply chain conscious procurement | 12.8.1 | Procuring construction materials that take into account economic, social, and environmental considerations in the production and distribution process | Not engaging in any of the following efforts (no applicable efforts), Engaging in one applicable effort, Actively engaging in two or more applicable efforts; 1) Procurement is conducted in consideration of economic aspects (e.g., payment of just compensation from the perspective of Creating Shared Value (CSV)). 2) Procurement is conducted in consideration of social cremation (e.g., checking the working environment of suppliers). 3) Procurement is conducted in consideration of environmental aspects (e.g., procurement of materials in accordance with the Green Procurement Guidelines). | All | SDGs original | [5 empty] | #DIV/0! | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | FALSE |  |  |  |  | 0 | #DIV/0! | FALSE | #DIV/0! | 3
Goal 13. Climate Action | 13.1 | Reduction of building WLC | 13.1.1 | Working toward carbon neutrality | Efforts are being made to reduce the WLC of buildings. | All | LR3.1 "Consideration of global warming" | #VALUE! | #VALUE! | #VALUE! | （The result for 7.8.1 is transferred.） |  | #VALUE! | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | #VALUE! |  | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | FALSE | #VALUE! | #VALUE!
| 13.2 | Reducing heat gain in urban spaces | 13.2.1 | Reduce thermal effects on surroundings | Efforts are being made to contribute to the reduction of off-site heat load, such as measures to reduce the heat island effect. | All | LR3.2.2 "Heat Island Effect" |  | ● |  | （The result for 3.8.4 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
| 13.3 | Reducing the impact of extreme weather on building | 13.3.1 | Take measures against typhoons and flying debris, floods, and landslides | Not engaging in any of the following efforts (no applicable efforts), Engaging in one applicable effort, Actively engaging in two or more applicable efforts; 1) Prepare for the possibility of increased damage from high winds in the future (design above and beyond building code, measures against flying debris in openings such as laminated glass, storm windows, shutters, etc.). 2) Preparing for flood damage that may increase in the future (confirming local characteristics that are less likely to be affected, consideration of electrical equipment, etc., and evacuation procedures). 3) Preparedness for possible increase in landslide disasters in the future (confirming local characteristics that are less likely to be affected and evacuation methods). 4) Evacuation measures for the elderly and other vulnerable groups in the event of a disaster (e.g., evacuation advisory with adequate time, transportation methods, preparation of medicines, etc.) | All | SDGs original | [5 empty] | #DIV/0! | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | FALSE |  |  |  |  | 0 | #DIV/0! | FALSE | #DIV/0! | 1.5
|  |  | 13.3.2 | Identify site hazards and share information | Not engaging in any of the following efforts (no applicable efforts), Actively engaging in one or more applicable efforts; 1) Confirm the hazard of the site using hazard maps, etc. 2) Share and disseminate information on disasters using digital signage, etc. | All | SDGs original | ● |  |  | （The result for 9.5.1 is transferred.） |  | 1 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | 1 |  |  |  |  | 1 | 1 | FALSE | 1
| 13.4 | Reducing the Impact of climate change on building users | 13.4.1 | Ensure a comfortable room temperature | The air conditioning system is designed to provide a comfortable room temperature even during peak load periods. | All | Q1.2.1.1 "Room temperature" |  | ● |  | （The result for 3.1.1 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
|  |  | 13.4.2 | Improving thermal insulation | Efforts are being made to reduce heat gain or loss from the outside of the building. | All | Q1.2.1.2 "Perimeter performance" |  | ● |  | （The result for 3.1.2 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 13.4.3 | Creating a homogeneous thermal environment | (i) Detailed zoning air conditioning is used to eliminate uneven temperatures in the indoor environment and create a comfortable environment. | Non-Sch, Non-Apt | Q1.2.1.3 "Zoned control" |  | ● |  | （The result for 3.1.3 is transferred.） |  | 2 | 事務所 |  | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル |  | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
[5 empty] | (ii) A type of air conditioning system is used to reduce the vertical temperature difference and airflow velocity (residual air velocity) in the occupied area. | All | Q1.2.3 "Type of air conditioning system" |  | ● |  |  |  |  | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2
| 13.5 | Introduction to resilient design | 13.5.1 | Protecting internal equipment | Measures are taken to protect its internal facilities. | All | Q2.2.1.1 "Earthquake-resistance (resistance to building breakage)" and Q2.2.1.2 "Seismic isolation, seismic & vibration control (internal equipment protection)" |  | ● |  | （The result for 9.4.1 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
|  |  | 13.5.2 | Ensure resilience of HVAC system | Efforts are being made to improve the reliability of the HVAC system. | All | Q2.2.4.1 "HVAC system" |  | ● |  | （The result for 9.4.2 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 13.5.3 | Ensure resilience of water supply & drainage and sanitation systems | Efforts are being made to improve the reliability of water supply & drainage and sanitation facilities. | All | Q2.2.4.2 "Water supply & drainage, sanitation" |  | ● |  | （The result for 6.7.1 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 13.5.4 | Ensure resilience of electrical equipment | Efforts are being made to secure power supply in case of emergency, such as power failure. (e.g., The facility equipped with emergency power generation equipment and uninterruptible power supply equipment, or the facility avoiding installation in underground spaces) | All | Q2.2.4.3 "Electrical equipment" |  | ● |  | （The result for 7.6.1 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 13.5.5 | Ensure resilience of support method of machines & ducts | Efforts are being made to improve the reliability of mechanical and piping supports. | All | Q2.2.4.4 "Support method of machines & ducts" |  | ● |  | （The result for 9.4.5 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
|  |  | 13.5.6 | Ensure resilience of communication wiring | Efforts are being made to improve the reliability of communications & IT equipment. | All | Q2.2.4.5 "Communications & IT equipment" |  | ● |  | （The result for 9.4.6 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2
Goal 14. Life Below Water | Assessment based on Goal 12: Responsible Consumption and Production, etc.
Goal 15. Life on Land | 15.1 | Consideration for greening of exterior, rooftop, and wall surfaces, and biodiversity conservation | 15.1.1 | Conservation of the biological environment | Initiatives that contribute to the preservation and creation of biotope are involved. | All | Q3.1 "Preservation and creation of biotope" |  | ● |  |  |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 2
| 15.2 | Soil contamination countermeasures | 15.2.1 | Preventing soil contamination | Not engaging in any of the following efforts (no applicable efforts), Actively engaging in one or more applicable efforts; 1) Conduct soil contamination survey 2) Excavation and removal of contaminated soil | All | SDGs original | ● |  |  | （The result for 6.4.1 is transferred.） |  | 1 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | 1 |  |  |  |  | 1 | 1 | FALSE | 1 | 1
| 15.3 | Sustainable use of resources | 15.3.1 | Procuring timber from sustainable forestry | Timber from sustainable forestry is used. | All | LR2.2.5 "Timber from sustainable forestry" |  | ● |  | （The result for 8.3.5 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 1.5
|  |  | 15.3.2 | Engage in the use of local resources | The use of materials with local characteristics (for structural materials, interior materials, exterior materials, exterior construction, etc.) is being considered. | All | Q3.3.1 "Attention to local characteristics & improvement of comfort - I 2) Use of materials with local characteristics" and Q3.2 "Attention to townscape and landscape 4) Formation of a good landscape with materials with local characteristics" | ● |  |  | （The result for 8.5.1 is transferred.） |  | 1 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 1 |  | 1 | 1 | 1 | 1 | FALSE | 1
| 15.4 | Reuse of wood generated during building disposal | 15.4.1 | Reusing old materials | Not engaging in any of the following efforts (no applicable efforts), Actively engaging in one or more applicable efforts; Reuse of domestic old wood | All | SDGs original | [5 empty] | 1 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | FALSE |  |  |  |  | 1 | 1 | FALSE | 1 | 1
Goal 16. Peace, Justice and Strong Institutions | Assessment based on Goal 12: Responsible Consumption and Production, etc.
Goal 17. Partnerships for the Goals | 17.1 | Consideration for suppliers when procuring materials | 17.1.1 | Procuring timber from sustainable forestry | Timber from sustainable forestry is used. | All | LR2.2.5 "Timber from sustainable forestry" |  | ● |  | （The result for 8.3.5 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 1.5
|  |  | 17.1.2 | Engage in the use of local resources | The use of materials with local characteristics (for structural materials, interior materials, exterior materials, exterior construction, etc.) is being considered. | All | Q3.3.1 "Attention to local characteristics & improvement of comfort - I 2) Use of materials with local characteristics" and Q3.2 "Attention to townscape and landscape 4) Formation of a good landscape with materials with local characteristics" | ● |  |  | （The result for 8.5.1 is transferred.） |  | 1 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 1 |  | 1 | 1 | 1 | 1 | FALSE | 1
| 17.2 | Building plans that facilitate communication | 17.2.1 | Create a favorable townscape and landscape | Efforts are being made for the surrounding townscape and landscape (use of materials suited to the characteristics of the area, planting of trees to create a good landscape) | All | Q3.2 "Consideration for townscape and landscape" |  | ● |  | （The result for 11.8.1 is transferred.） |  | 2 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 3 | 0 | 3 | 2 | 2 | 2 | FALSE | 2 | 1.5
|  |  | 17.2.2 | Encourage community participation | Efforts are being made to encourage the participation of local residents in the operation and management of the building. | All | Q3.3.1 "Attention to local characteristics & improvement of comfort - V Involvement of building users, etc. " | ● |  |  | （The result for 11.3.1 is transferred.） |  | 1 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 |  | 1 |  | 1 | 1 | 1 | 1 | FALSE | 1 | 1
| 17.3 | Supply chain management, creating shared value | 17.3.1 | Work with stakeholders to improve economic, social, and environmental conditions in production and distribution processes | Not engaging in any of the following efforts (no applicable efforts), Actively engaging in one or more applicable efforts; 1) Identify the economic, social, and environmental improvement initiatives of suppliers of parts and materials for products, and determine whether or not to collaborate with them. 2) Utilize AI and IoT technologies to enhance collaboration with stakeholders. | All | SDGs original | [5 empty] | 3 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | FALSE |  |  |  |  | 0 | 3 | FALSE | 3 | 3
| 17.4 | Introduction of after-sales service system | 17.4.1 | Provide after-sales service | Not engaging in any of the following efforts (no applicable efforts), Actively engaging in one or more applicable efforts; Management of basic building information and maintenance history to enable follow-up investigations in the event of defects | All | SDGs original | [5 empty] | 3 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | FALSE |  |  |  |  | 0 | 3 | FALSE | 3 | 3
| 17.5 | ICT environment that facilitates communication | 17.5.1 | Provide ICT environment | Not engaging in any of the following efforts (no applicable efforts), Actively engaging in one or more applicable efforts; Introduction of regional communication services utilizing ICT technology (disaster prevention information, energy management, regional monitoring service, community activities, etc.) | All | SDGs original | [5 empty] | 3 | 事務所 | 学校 | 物販店 | 飲食店 | 集会所 | 工場 | 病院 | ホテル | 集合住宅 | 対象 | FALSE |  |  |  |  | 0 | 3 | FALSE | 3 | 3
N.A.
N.A.
[23 empty] | N.A. | [9 empty] | 5点満点換算 | 実施しない
[23 empty] | N.A. | [5 empty] | 総合点 |  | #VALUE! | → | #VALUE! | #VALUE!
[23 empty] | N.A. | [8 empty] | 実施しない
[23 empty] | N.A. | [5 empty] | ゴール3 |  | 2.1429 | 2.1429
[23 empty] | N.A. | [5 empty] | ゴール4 |  | 2 | 2
[23 empty] | N.A. | [5 empty] | ゴール5 |  | 2 | 2
[23 empty] | N.A. | [5 empty] | ゴール6 |  | 1.7857 | 1.7857
[23 empty] | N.A. | [5 empty] | ゴール7 |  | #VALUE! | #VALUE!
[23 empty] | N.A. | [5 empty] | ゴール8 |  | 2 | 2
[23 empty] | N.A. | [5 empty] | ゴール9 |  | 1.75 | 1.75
[23 empty] | N.A. | [5 empty] | ゴール11 |  | 1.8833 | 1.8833
[23 empty] | N.A. | [5 empty] | ゴール12 |  | #VALUE! | #VALUE!
[23 empty] | N.A. | [5 empty] | ゴール13 |  | #VALUE! | #VALUE!
[23 empty] | N.A. | [5 empty] | ゴール15 |  | 1.375 | 1.375
[23 empty] | N.A. | [5 empty] | ゴール17 |  | 2.1667 | 2.1667
3
aaaa

## Std.
n WLC Calculation Conditions Sheet (Standard Calc) |  |  | n Building Name | XXX Building
CASBEE-BD_NCe_2024_v1.21
Items |  | Reference Building | Evaluated Building | Note
Building Overview | Building type | Offices, | Offices,
| Gross floor area | 7000 | 7000
| Structure | RC | RC
Life Cycle | Estimated service life | 60years(Office,) | 60years(Office,)
| GHG emissions | 18.22 | 18.22 | kg-CO2eq/yr-㎡
| (Included GHG by installation of renewables) | － | 0 | kg-CO2eq/yr-㎡
Con-struction Stage | Embodied carbon calculation method | The standard calculation methods of “J-CAT®” by IBECs | Estimated by subtracting GHG reduction due to recycled material use from GHG of reference building.
| Reference for GHG emission intensity | AIJ-LCA intensity database by analytical data of the 2015 Industrial Input-Output Table | See reference building
| Boundary | National and international final consumption. | See reference building
Quantities of Representative Materials
| Regular concrete | 0.696 | 0.696 | m3/m2
| Blast furnace cement concrete | 0 | 0 | m3/m2
| Formwork | 0.6675 | 0.6675 | m2/m2
| Reinforcing bars | 0.078 | 0.078 | t/m2
| Steel frame | 0.1 | 0.1 | t/m2
| Deck plate | 0 | 0 | m2/m2
| □ □ | ○○ | 〃
GHG emission intensities of Representative Materials
| Regular concrete | 315.84 | See reference building | kg-CO2eq/m3
| Blast furnace cement concrete | 257.14 | See reference building | kg-CO2eq/m3
| Steel frame | 1.41 | See reference building | kg-CO2eq/kg
| Steel frame (blast furnace) | 1.41 | See reference building | kg-CO2eq/kg
| Reinforcing bars | 1 | See reference building | kg-CO2eq/kg
| Formwork | 7.45 | See reference building | kg-CO2eq/㎡
| Deck plate | 37.64 | See reference building | kg-CO2eq/㎡
Main recycled materials and usage
| Blast furnace cement (structural use) | 0%
| Existing frame materials (structural use) | 0%
| Electric furnace steel (reinforcement) | 0% | 0%
| Electric furnace steel (steel materials) | 0% | 0%
| GHG emissions | 20.11 | 20.11 | kg-CO2eq/yr-㎡
Repair, | (Included GHG by installation of renewables) | － | 0 | kg-CO2eq/yr-㎡
Renewal/ | Upgrade period (year)
Demolition | Exterior | 25 | 25
Roof
Stage | Interior | 18 | 18
| Building Service | 15 | 15
Average repair rate (%/year)
| Exterior | 1% | 1%
| Interior | 1% | 1%
| Building Service | 2% | 2%
| Calc method for demolition-related GH | Assuming road transport distance of 30 km for demolition materials | See reference building
GHG emissions
| [1] Reference value/ [2] Building-related initiatives | #VALUE! | #VALUE! | kg-CO2eq/yr-㎡
| [3] Above + other on-site initiatives | － | #VALUE! | kg-CO2eq/yr-㎡
|  | Reduced GHG by PV |  | kg-CO2eq/yr-㎡
|  | (Breakdown) In-house consumption | #VALUE! | kg-CO2eq/yr-㎡
|  | Excess power sold | #VALUE! | kg-CO2eq/yr-㎡
|  | Other renewable energy | －
Operation | [4] Above + other off-site measures | － | #VALUE! | kg-CO2eq/yr-㎡
stage | Reference | (a) Carbon offsetting with renewable energy certificates | －
|  | (b) Carbon offsetting with green heat certificate | －
|  | (c) Other carbon credit | －
|  | (d) Difference between basic and adjusted emissions (obtained from the adjusted emission factor) | －
－
| 棒グラフ | ③ | #VALUE! | kg-CO2eq/年㎡
|  | ④ | #VALUE! | kg-CO2eq/年㎡
| Calculation method for energy consumption | Average primary energy consumptions based on statistical value | Estimated based on energy conservation achieved with LR1-related measures
| Primary energy consumption | 10850 | 2712.5 | GJ/yr
GHG emission factors for energy
| Primary energy Non-residential buildings | #VALUE! | See reference building | kg-CO2eq/MJ
| Primary energy Residential buildings (Dwelling areas) | #VALUE! | See reference building | kg-CO2eq/MJ
| Electricity | #VALUE! | See reference building | kg-CO2eq/kWh
| Gas | 0.0456 | See reference building | kg-CO2eq/MJ
| Other fuels ( ) | ○○ | See reference building | kg-CO2eq/MJ
Potable water
|  | － | － | Out of scope
Other |  |  | "XX" is introduced as off-site measures

## Indiv.
n WLC Calculation Conditions Sheet (Individual Calc) |  |  | n Building Name | XXX Building
CASBEE-BD_NCe_2024_v1.21
Items | 0 | Reference Building | Evaluated Building | Note
Building Overview | Building type | Offices, | Offices,
| Gross floor area | 7000 | 7000
| Structure | RC | RC
Life Cycle | Estimated service life | ○○ | ○○
| GHG emissions | 35 | 30 | kg-CO2eq/yr-㎡
| (Included GHG by installation of renewables) | － | 1 | kg-CO2eq/yr-㎡
Con-struction Stage | Embodied carbon calculation method | 〇〇 | 〇〇
0 | Reference for GHG emission intensity | 〇〇 | 〇〇
0 | Boundary | 〇〇 | 〇〇
0 | Quantities of Representative Materials
0 | Regular concrete | ○○ | ○○ | m3/m2
0 | Blast furnace cement concrete | ○○ | ○○ | m3/m2
0 | Formwork | ○○ | ○○ | m2/m2
0 | Reinforcing bars | ○○ | ○○ | t/m2
0 | Steel frame | ○○ | ○○ | t/m2
0 | Deck plate | ○○ | ○○ | m2/m2
0 | □ □ | ○○ | ○○
0 | GHG emission intensities of Representative Materials
0 | Regular concrete | ○○ | See reference building | kg-CO2eq/m3
0 | Blast furnace cement concrete | ○○ | See reference building | kg-CO2eq/m3
0 | Steel frame | ○○ | See reference building | kg-CO2eq/kg
0 | Steel frame (blast furnace) | ○○ | See reference building | kg-CO2eq/kg
0 | Reinforcing bars | ○○ | See reference building | kg-CO2eq/kg
0 | Formwork | ○○ | See reference building
0 | Deck plate | ○○ | See reference building
0 | Main recycled materials and usage
0 | Blast furnace cement (structural use) | ○○ | ○○
0 | Existing frame materials (structural use) | ○○ | ○○
0 | Electric furnace steel (reinforcement) | ○○ | ○○
0 | Electric furnace steel (steel materials) | ○○ | ○○
| GHG emissions | 10 | 8 | kg-CO2eq/yr-㎡
Repair, | (Included GHG by installation of renewables) | － | 0.5 | kg-CO2eq/yr-㎡
Renewal/ | Upgrade period (year)
Demolition | Exterior | 〇〇 | 〇〇
0 | Roof | 〇〇 | 〇〇
Stage | Interior | 〇〇 | 〇〇
| Building Service | 〇〇 | 〇〇
Average repair rate (%/year)
| Exterior | 〇〇 | 〇〇
| Interior | 〇〇 | 〇〇
| Building Service | 〇〇 | 〇〇
| Calc method for demolition-related GH | 〇〇 | 〇〇
GHG emissions
| [1] Reference value/ [2] Building-related initiatives | 30 | 20 | kg-CO2eq/yr-㎡
| [3] Above + other on-site initiatives | － | 10 | kg-CO2eq/yr-㎡
|  | Reduced GHG by PV | 10 | kg-CO2eq/yr-㎡
|  | (Breakdown) In-house consumption | 5 | kg-CO2eq/yr-㎡
|  | Excess power sold | 5 | kg-CO2eq/yr-㎡
Other renewable energy
Operation | [4] Above + other off-site measures | － | 5 | kg-CO2eq/yr-㎡
stage | Reference | (a) Carbon offsetting with renewable energy certificates | 5 | kg-CO2eq/yr-㎡
(b) Carbon offsetting with green heat certificate
(c) Other carbon credit
(d) Difference between basic and adjusted emissions (obtained from the adjusted emission factor)
| 棒グラフ | ③ | 49.5 | kg-CO2eq/年㎡
| 0 | ④ | 44.5 | kg-CO2eq/年㎡
| Calculation method for energy consumption | 〇〇 | 〇〇
| Primary energy consumption | ○○ | ○○ | GJ/年
GHG emission factors for energy
| Primary energy Non-residential buildings | ○○ | See reference building | kg-CO2eq/MJ
| Primary energy Residential buildings (Dwelling areas) | ○○ | See reference building | kg-CO2eq/MJ
| Electricity | ○○ | See reference building | kg-CO2eq/kWh
| Gas | ○○ | See reference building | kg-CO2eq/MJ
| Other fuels ( ) | ○○ | See reference building | kg-CO2eq/MJ
Potable water
Other
0
0
0
<Ref.> Values available for individual calculation
Reduction in GHG emissions with use of solar power (when the amount of power generated is equivalent to the reduction in "3. On-site measures," and when the emission factor for electricity is used to estimate the reduced amount.)
| Solar-generated power | Total | 277920.082 | kWh/yr
Operation |  | In-house consumption | 277920.082 | kWh/yr
Stage |  | Excess power sold | 0 | kWh/yr
| Reduction | Total [1] | #VALUE! | kg-CO2/yr-㎡
| in GHG emission | In-house consumption | #VALUE! | kg-CO2/yr-㎡
|  | Excess power sold | #VALUE! | kg-CO2/yr-㎡
| 算定に用いた排出係数 | 自家消費分 | #VALUE! | kg-CO2/kWh
|  | 余剰売電分 | #VALUE! | kg-CO2/kWh
|  | 備考 | 基礎排出係数の場合
Difference between basic emissions and emission using adjusted emission factor
| Electricity consumption of the eval. bldg. in "3. On-site measures". |  | 216777.6639 | kWh/yr
| Emission factors | Basic emission factor | #VALUE! | kg-CO2/kWh
|  | Adjusted emission factor | 0.04 | kg-CO2/kWh
| Difference over | Entire building | #VALUE! | kg-CO2/yr-㎡
| basic emission | Per gross floor area [2] | #VALUE! | kg-CO2/yr-㎡
Note on D50: See <Ref.> below, and the value [1] can be referred.
Note on D58: See <Ref.> below, and the value [2] can be referred.

## GHG data
n GHG Data base
| a. GHG Emissions Related to Construction | [5 empty] | Q2/2.2.1 Service Life of Structural Frame Materials
|  | kg-CO2eq/yr-m2 |  |  |  |  | S | ,Wood |  | RC |  |  | SRC
| Building Type | [5 empty] | Level 3 | Level 4 | Level 5 | Level 3 | Level 4 | Level 5 | Level 3 | Level 4 | Level 5
[5 empty] | 1 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
| Office |  |  |  | 10 |  | 19.23 | 19.23 | 19.23 | 17.62 | 17.62 | 17.62 | 18.22 | 18.22 | 18.22
|  | LR2.2.2 Existing structural frame |  | 100% | 11 |  | 8.05 | 8.05 | 8.05 | 8.09 | 8.09 | 8.09 | 7.99 | 7.99 | 7.99
|  | LR2.2.3 Recycled materials (Use of blast furnace cement) |  | 100% | 12 |  | 18.46 | 18.46 | 18.46 | 16.56 | 16.56 | 16.56 | 17.28 | 17.28 | 17.28
|  | LR2/2.2 削減分 |  |  | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | LR2/2.3 削減分 |  |  | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 合計 |  |  | 15 |  | 19.23 | 19.23 | 19.23 | 17.62 | 17.62 | 17.62 | 18.22 | 18.22 | 18.22
| School |  |  |  | 20 |  | 14.38 | 14.38 | 14.38 | 16.1 | 16.1 | 16.1 | 18.59 | 18.59 | 18.59
|  | LR2.2.2 Existing structural frame |  | 100% | 21 |  | 6.41 | 6.41 | 6.41 | 6.56 | 6.56 | 6.56 | 6.37 | 6.37 | 6.37
|  | LR2.2.3 Recycled materials (Use of blast furnace cement) |  | 100% | 22 |  | 13.9 | 13.9 | 13.9 | 14.89 | 14.89 | 14.89 | 17.29 | 17.29 | 17.29
|  | LR2/2.2 削減分 |  |  | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | LR2/2.3 削減分 |  |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 合計 |  |  | 25 |  | 14.38 | 14.38 | 14.38 | 16.1 | 16.1 | 16.1 | 18.59 | 18.59 | 18.59
| Retailers |  |  |  | 30 |  | 23.93 | 23.93 | 23.93 | 31.51 | 31.51 | 31.51 | 22.88 | 22.88 | 22.88
|  | LR2.2.2 Existing structural frame |  | 100% | 31 |  | 11.29 | 11.29 | 11.29 | 11.35 | 11.35 | 11.35 | 11.21 | 11.21 | 11.21
|  | LR2.2.3 Recycled materials (Use of blast furnace cement) |  | 100% | 32 |  | 23 | 23 | 23 | 29.02 | 29.02 | 29.02 | 22.05 | 22.05 | 22.05
|  | LR2/2.2 削減分 |  |  | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | LR2/2.3 削減分 |  |  | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 合計 |  |  | 35 |  | 23.93 | 23.93 | 23.93 | 31.51 | 31.51 | 31.51 | 22.88 | 22.88 | 22.88
| Restaurants |  |  |  | 40 |  | 23.93 | 23.93 | 23.93 | 31.51 | 31.51 | 31.51 | 22.88 | 22.88 | 22.88
|  | LR2.2.2 Existing structural frame |  | 100% | 41 |  | 11.29 | 11.29 | 11.29 | 11.35 | 11.35 | 11.35 | 11.21 | 11.21 | 11.21
|  | LR2.2.3 Recycled materials (Use of blast furnace cement) |  | 100% | 42 |  | 23 | 23 | 23 | 29.02 | 29.02 | 29.02 | 22.05 | 22.05 | 22.05
|  | LR2/2.2 削減分 |  |  | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | LR2/2.3 削減分 |  |  | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 合計 |  |  | 45 |  | 23.93 | 23.93 | 23.93 | 31.51 | 31.51 | 31.51 | 22.88 | 22.88 | 22.88
| Halls |  |  |  | 50 |  | 16.23 | 16.23 | 16.23 | 17.41 | 17.41 | 17.41 | 17.92 | 17.92 | 17.92
|  | LR2.2.2 Existing structural frame |  | 100% | 51 |  | 7.29 | 7.29 | 7.29 | 7.33 | 7.33 | 7.33 | 7.24 | 7.24 | 7.24
|  | LR2.2.3 Recycled materials (Use of blast furnace cement) |  | 100% | 52 |  | 15.76 | 15.76 | 15.76 | 16.19 | 16.19 | 16.19 | 16.75 | 16.75 | 16.75
|  | LR2/2.2 削減分 |  |  | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | LR2/2.3 削減分 |  |  | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 合計 |  |  | 55 |  | 16.23 | 16.23 | 16.23 | 17.41 | 17.41 | 17.41 | 17.92 | 17.92 | 17.92
| Factories |  |  |  | 60 |  | 25.13 | 25.13 | 25.13 | 28.4 | 28.4 | 28.4 | 30.17 | 30.17 | 30.17
|  | LR2.2.2 Existing structural frame |  | 100% | 61 |  | 11.03 | 11.03 | 11.03 | 11.13 | 11.13 | 11.13 | 11.22 | 11.22 | 11.22
|  | LR2.2.3 Recycled materials (Use of blast furnace cement) |  | 100% | 62 |  | 24.17 | 24.17 | 24.17 | 26.3 | 26.3 | 26.3 | 28.32 | 28.32 | 28.32
|  | LR2/2.2 削減分 |  |  | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | LR2/2.3 削減分 |  |  | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 合計 |  |  | 65 |  | 25.13 | 25.13 | 25.13 | 28.4 | 28.4 | 28.4 | 30.17 | 30.17 | 30.17
| Hospitals |  |  |  | 70 |  | 14.42 | 14.42 | 14.42 | 16.5 | 16.5 | 16.5 | 18.17 | 18.17 | 18.17
|  | LR2.2.2 Existing structural frame |  | 100% | 71 |  | 7.98 | 7.98 | 7.98 | 8.02 | 8.02 | 8.02 | 7.92 | 7.92 | 7.92
|  | LR2.2.3 Recycled materials (Use of blast furnace cement) |  | 100% | 72 |  | 13.99 | 13.99 | 13.99 | 15.45 | 15.45 | 15.45 | 17.08 | 17.08 | 17.08
|  | LR2/2.2 削減分 |  |  | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | LR2/2.3 削減分 |  |  | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 合計 |  |  | 75 |  | 14.42 | 14.42 | 14.42 | 16.5 | 16.5 | 16.5 | 18.17 | 18.17 | 18.17
| Hotels |  |  |  | 80 |  | 17.08 | 17.08 | 17.08 | 19.13 | 19.13 | 19.13 | 19.72 | 19.72 | 19.72
|  | LR2.2.2 Existing structural frame |  | 100% | 81 |  | 8.78 | 8.78 | 8.78 | 8.83 | 8.83 | 8.83 | 8.72 | 8.72 | 8.72
|  | LR2.2.3 Recycled materials (Use of blast furnace cement) |  | 100% | 82 |  | 16.49 | 16.49 | 16.49 | 17.76 | 17.76 | 17.76 | 18.61 | 18.61 | 18.61
|  | LR2/2.2 削減分 |  |  | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | LR2/2.3 削減分 |  |  | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 合計 |  |  | 85 |  | 17.08 | 17.08 | 17.08 | 19.13 | 19.13 | 19.13 | 19.72 | 19.72 | 19.72
| Apartments |  |  |  | 90 |  | 21.95 | 10.97 | 7.32 | 28.77 | 14.39 | 9.59 | 33.92 | 16.96 | 11.31
|  | LR2.2.2 Existing structural frame |  | 100% | 91 |  | 10.95 | 5.47 | 3.65 | 11.17 | 5.58 | 3.72 | 11.28 | 5.64 | 3.76
|  | LR2.2.3 Recycled materials (Use of blast furnace cement) |  | 100% | 92 |  | 21.03 | 10.52 | 7.01 | 26.65 | 13.32 | 8.88 | 31.73 | 15.86 | 10.58
|  |  | LR2/2.2 削減分 |  | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | LR2/2.3 削減分 |  | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 合計 |  | 95 |  | 21.95 | 10.97 | 7.32 | 28.77 | 14.39 | 9.59 | 33.92 | 16.96 | 11.31
| b. GHG Emissions Related to Repair, Renewal and Demolition | [5 empty] | Level 3 3: Q2/2.2.1 Service Life of Structural Frame Materials
|  | kg-CO2eq/yr-m2 |  |  |  |  | Level 3 3: S; Level 4 4: ,Wood; Level 3 6: RC; Level 3 9: SRC
| Building Type | [5 empty] | Level 3 | Level 4 | Level 5 | Level 3 | Level 4 | Level 5 | Level 3 | Level 4 | Level 5
| Office |  |  |  | 1 |  | 20.11 | 20.11 | 20.11 | 20.42 | 20.42 | 20.42 | 20.11 | 20.11 | 20.11
|  | LR2/2.2 既存建築躯体 |  | 100%
|  | 削減後 |  |  |  | 0% | 20.11 | 20.11 | 20.11 | 20.42 | 20.42 | 20.42 | 20.11 | 20.11 | 20.11
| School |  |  |  | 2 |  | 13.93 | 13.93 | 13.93 | 14.83 | 14.83 | 14.83 | 14.59 | 14.59 | 14.59
|  | LR2/2.2 既存建築躯体 |  | 100%
|  | 削減後 |  |  |  | 0% | 13.93 | 13.93 | 13.93 | 14.83 | 14.83 | 14.83 | 14.59 | 14.59 | 14.59
| Retailers |  |  |  | 3 |  | 8.82 | 8.82 | 8.82 | 10.28 | 10.28 | 10.28 | 8.71 | 8.71 | 8.71
|  | LR2/2.2 既存建築躯体 |  | 100%
|  | 削減後 |  |  |  | 0% | 8.82 | 8.82 | 8.82 | 10.28 | 10.28 | 10.28 | 8.71 | 8.71 | 8.71
| Restaurants |  |  |  | 4 |  | 8.82 | 8.82 | 8.82 | 10.28 | 10.28 | 10.28 | 8.71 | 8.71 | 8.71
|  | LR2/2.2 既存建築躯体 |  | 100%
|  | 削減後 |  |  |  | 0% | 8.82 | 8.82 | 8.82 | 10.28 | 10.28 | 10.28 | 8.71 | 8.71 | 8.71
| Halls |  |  |  | 5 |  | 17.05 | 17.05 | 17.05 | 17.76 | 17.76 | 17.76 | 17.54 | 17.54 | 17.54
|  | LR2/2.2 既存建築躯体 |  | 100%
|  | 削減後 |  |  |  | 0% | 17.05 | 17.05 | 17.05 | 17.76 | 17.76 | 17.76 | 17.54 | 17.54 | 17.54
| Factories |  |  |  | 6 |  | 9.04 | 9.04 | 9.04 | 10.1 | 10.1 | 10.1 | 9.96 | 9.96 | 9.96
|  | LR2/2.2 既存建築躯体 |  | 100%
|  | 削減後 |  |  |  | 0% | 9.04 | 9.04 | 9.04 | 10.1 | 10.1 | 10.1 | 9.96 | 9.96 | 9.96
| Hospitals |  |  |  | 7 |  | 19.17 | 19.17 | 19.17 | 19.54 | 19.54 | 19.54 | 19.66 | 19.66 | 19.66
|  | LR2/2.2 既存建築躯体 |  | 100%
|  | 削減後 |  |  |  | 0% | 19.17 | 19.17 | 19.17 | 19.54 | 19.54 | 19.54 | 19.66 | 19.66 | 19.66
| Hotels |  |  |  | 8 |  | 21.92 | 21.92 | 21.92 | 22.7 | 22.7 | 22.7 | 22.25 | 22.25 | 22.25
|  | LR2/2.2 既存建築躯体 |  | 100%
|  | 削減後 |  |  |  | 0% | 21.92 | 21.92 | 21.92 | 22.7 | 22.7 | 22.7 | 22.25 | 22.25 | 22.25
| Apartments |  |  |  | 9 |  | 9.48 | 11.33 | 11.82 | 10.68 | 12.06 | 12.39 | 10.89 | 12.24 | 12.55
|  | LR2/2.2 既存建築躯体 |  | 100%
|  | 削減後 |  |  |  | 0% | 9.48 | 11.33 | 11.82 | 10.68 | 12.06 | 12.39 | 10.89 | 12.24 | 12.55
c. GHG Emissions Related to Operational Energy
emission factors
|  | Electricity (basic factor) |  | kg-CO2eq/kWh |  |  | Level 3: #VALUE!; Level 4: XXX; Level 4: （Adjusted emission factor; Level 3: 0.04; Level 4: kg-CO2eq/kWh）
|  |  |  | kg-CO2eq/MJ |  |  | Level 3: #VALUE!; Level 4: 9.76; Level 5: MJ/kWh conversion （all day average in Notification No. 265 of MLIT, 2016) |  |  |  |  | 0.0040984
|  | Town gas |  | kg-CO2eq/MJ |  |  | Level 3: 0.0456; Level 4: alternative coefficient value=2.05 [t-CO2/kilo-m3] / [45MJ/m3] (List of emission factors by gas supplier (for submission in 2024), June 28, 2024)
|  | DHC (heat energy) |  | kg-CO2eq/MJ |  |  | Level 3: 0.0532; Level 4: alternative coefficient value=0.0532 [t-CO2/GJ] (List of emission factors by heat supplier (for submission in 2024), June 28, 2024)
|  | Kerosene |  | kg-CO2eq/MJ |  |  | Level 3: 0.0686; Level 4: *
|  | Type A heavy oil |  | kg-CO2eq/MJ |  |  | Level 3: 0.0708; Level 4: *
|  | Other |  | kg-CO2eq/MJ |  |  | Level 3: 0.0697; Level 4: (Average value for kerosene + type A heavy oil)
|  | LPG |  | kg-CO2eq/MJ |  |  | Level 3: 0.0598; Level 4: *
[7 empty] | * Source; | Calculation Methods and Emission Factors List under the Calculation, Reporting, and Disclosure System (MOE, Updated December 12, 2024 (Partially revised July 11, 2025))
Examples of published emission factors by electricity supplier (for calculating greenhouse gas emissions by specified emitters) - FY2022 results - (August 29, 2024)
|  | Name of company |  | (t-CO2/kWh) |  |  | Level 3: Basic / alternative factors; Level 5: ＜Ref.＞adjusted emission factors
|  | Hokkaido Electric Power Co., Inc. |  |  |  | 1 | Level 3: 0.000533; Level 5: 0.000535
|  | Tohoku Electric Power Co., Inc. |  |  |  | 2 | Level 3: 0.000477; Level 5: 0.00046
|  | TEPCO Energy Partner, Inc. |  |  |  | 3 | Level 3: 0.000457; Level 5: 0.000376
|  | Chubu Electric Power Miraiz Co., Inc. |  |  |  | 4 | Level 3: 0.000433; Level 5: 0.00044
|  | Hokuriku Electric Power Co., Inc. |  |  |  | 5 | Level 3: 0.000487; Level 5: 0.000499
|  | Kansai Electric Power Co., Inc. |  |  |  | 6 | Level 3: 0.00036; Level 5: 0.00042
|  | Chugoku Electric Power Co., Inc. |  |  |  | 7 | Level 3: 0.000537; Level 5: 0.000544
|  | Shikoku Electric Power Co., Inc. |  |  |  | 8 | Level 3: 0.00037; Level 5: 0.000447
|  | Kyushu Electric Power Co., Inc. |  |  |  | 9 | Level 3: 0.000407; Level 5: 0.000462
|  | Okinawa Electric Power Co., Inc. |  |  |  | 10 | Level 3: 0.00071; Level 5: 0.000675
|  | Alternative coefficient value |  |  |  |  | Level 3: 0.000429
Primary energy (consumption) intensities by building type
|  | Building Type |  |  |  | 評価建物 | Level 3: Primary energy consumption intensities by building size [MJ/m2-yr]; Level 5: Primary energy source composition ratio |  | GHG conversion coefficients
[7 empty] | 300 | 2000 | 10000 | 30000 |  | #VALUE! | 0.0456 | 0.0697 | 0.0598 | 0.0532
[7 empty] | less than 300m2 | over 300m2 and less that 2,000m2 | over 2,000m2 and less that 10,000m2 | over 10,000m2 and less that 30,000m2 | over 30,000m2 | Electricity | Town gas | Other * | LPG | Heat | kg-CO2eq/MJ
|  | Office | Office |  | 7000 | 1550 | 1250 | 1250 | 1550 | 1850 | 2150 | 78% | 6% | 16% | - | - | #VALUE!
|  |  | Government buildings |  | 0 | 0 | 1050 | 1050 | 1050 | 1050 | 1050 | 77% | 9% | 14% | - | - | #VALUE!
|  |  | Research institutes |  | 0 | 0 | 2350 | 2350 | 2350 | 2350 | 2350 | 63% | 8% | 29% | - | - | #VALUE!
|  | School | Kindergartens/ nursery schools |  | 0 | 0 | 540 | 540 | 540 | 540 | 540 | 70% | 12% | 18% | - | - | #VALUE!
|  |  | ES/JHS | Hokkaido | 0 | 0 | 510 | 510 | 510 | 510 | 510 | 67% | 20% | 13% | - | - | #VALUE!
|  |  |  | Other area | 0 | 0 | 320 | 320 | 320 | 320 | 320 | 74% | 12% | 14% | - | - | #VALUE!
|  |  | High schools |  | 0 | 0 | 360 | 360 | 360 | 360 | 360 | 74% | 7% | 19% | - | - | #VALUE!
|  |  | Universities/ colleges |  | 0 | 0 | 860 | 860 | 860 | 860 | 1100 | 66% | 11% | 23% | - | - | #VALUE!
|  | Retailers | Department, supermarkets |  | 0 | 0 | 7250 | 7250 | 5000 | 2950 | 2950 | 73% | 4% | 23% | - | - | #VALUE!
|  |  | Convenience store |  | 0 | 0 | 12900 | 12900 | 12900 | 12900 | 12900 | 100% | 0% | 0% | - | - | #VALUE!
|  |  | Electronics retailers, |  | 0 | 0 | 2850 | 2850 | 2850 | 2850 | 2850 | 71% | 1% | 28% | - | - | #VALUE!
|  |  | Other stores |  | 0 | 0 | 2300 | 2300 | 2300 | 2300 | 2300 | 89% | 3% | 8% | - | - | #VALUE!
|  | Restaurants |  |  | 0 | 0 | 19350 | 11950 | 3150 | 3150 | 3150 | 51% | 33% | 16% | - | - | #VALUE!
|  | Halls | Theatres/halls |  | 0 | 0 | 1350 | 1350 | 1350 | 1400 | 1400 | 73% | 13% | 14% | - | - | #VALUE!
|  |  | Exhibition facilities |  | 0 | 0 | 1100 | 1100 | 1100 | 1100 | 1100 | 77% | 7% | 16% | - | - | #VALUE!
|  |  | Sports facilities |  | 0 | 0 | 1850 | 1850 | 1850 | 1850 | 1850 | 69% | 16% | 15% | - | - | #VALUE!
|  | Factories |  |  | 0 | 0 | 500 | 500 | 500 | 500 | 500 | 100% | 0% | 0% | - | - | #VALUE!
|  | Hospitals |  |  | 0 | 0 | 2200 | 2200 | 2200 | 2450 | 2950 | 48% | 13% | 39% | - | - | #VALUE!
|  | Hotels |  |  | 0 | 0 | 2450 | 2450 | 2450 | 2750 | 2750 | 42% | 14% | 44% | - | - | #VALUE!
[5 empty] | 0 | 0 | [10 empty] | #VALUE!
|  | Apartments | Dwelling area |  |  | - | - | - | - | - | - | 52.1% | 22.7% | 14.7% | 10.1% | 0.1% | #VALUE! | →24年版見直し
|  |  | Common area |  |  | 0 | Level 3: 522 (outdoor corridor) /801 (indoor corridor); Level 5: 100%; Level 3: 0%; Level 4: 0%; Level 5: - | - | #VALUE!
|  | 評価建物 | [14 empty] | #VALUE! | bar: Level 3 to Level 4; Level 5
|  | Source; | Data summarised from DECC data-base for Energy Consumption of Commercial Building (released in 2019, JSBC).L153 |  |  |  | Level 4: * Kerosene for Apt.
"Transition of final energy consumption by energy source type in residential sector (Energy demand and supply record in FY 2022, General Affairs Division Strategic Planning Office, the Agency of Natural Resources and Energy)"
Regarding factories, since there is no statistical data available, the energy consumption for lighting in office buildings under the Notification No. 265 of MLIT of 2016 is used.
|  | LR1.3 Primary energy consumption intensities based on housing specification standards for GHG emissions calculation (other energy consumption by home appliances etc. included) | [27 empty] | 基準一次エネルギー（その他含む）MJ |  |  |  | ※その他 | 21241 | MJ | ※面積 | 120.08 | ㎡
|  | Type of HVAC |  | Levels |  |  | Evaluated Bld. | Regional classification | [5 empty] | MJ/yr-m2 | [15 empty] | 設備の方式 |  | １地域 | ２地域 | ３地域 | ４地域 | ５地域 | ６地域 | ７地域 | ８地域
|  | Heating | Cooling | in LR1.3 |  | 1 | 3 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |  | 地域区分 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |  |  | 暖房 | 冷房
|  |  |  | Reference | Aa0 | 2 | 1119.7618 | 1427.4067 | 1258.0197 | 1119.7618 | 1120.2448 | 1036.3757 | 940.7728 | 817.3384 | 853.2895 |  |  | 評価建物 | 1552.4584 | 1366.1326 | 1214.049 | 1214.5803 | 1122.3243 | 1017.1611 | 881.3832 | 920.9294 | [5 empty] | 171403 | 151063 | 134461 | 134519 | 124448 | 112968 | 98146 | 102463
|  | Ａ | ａ | Level 1 | Aa1 | 3 | 1214.049 | 1552.4584 | 1366.1326 | 1214.049 | 1214.5803 | 1122.3243 | 1017.1611 | 881.3832 | 920.9294 |  |  | 参照値 | 1427.4067 | 1258.0197 | 883.5276 | 902.1153 | 843.3628 | 828.3228 | 750.6496 | 853.2895 |  |  |  | Ａ | ａ | 171403 | 151063 | 134461 | 134519 | 124448 | 112968 | 98146 | 102463
|  |  |  | Level 2 | Aa2 | 4 | 1119.7618 | 1427.4067 | 1258.0197 | 1119.7618 | 1120.2448 | 1036.3757 | 940.7728 | 817.3384 | 853.2895 |  |  | 方式（参照値） | Aa | Aa | Ba | Ba | Ba | Ba | Ba | Aa |  |  |  | 住戸全体 | 住戸全体 | 171403 | 151063 | 134461 | 134519 | 124448 | 112968 | 98146 | 102463
|  |  |  | Level 4 | Aa4 | 5 | 931.1875 | 1177.3035 | 1041.7938 | 931.1875 | 931.574 | 864.4787 | 787.9963 | 689.2488 | 718.0097 | [14 empty] | ダクトセントラル | ダクトセントラル | 171403 | 151063 | 134461 | 134519 | 124448 | 112968 | 98146 | 102463
|  |  |  | Reference | Ab0 | 6 | 1099.1922 | 1413.7825 | 1245.4697 | 1099.1922 | 1084.5686 | 1001.9154 | 864.6569 | 718.6626 | 573.7175 | [6 empty] | 参照値（レベル３） | 1 | ←2024年版＝1.0（レベル２） 戸建は0.9（レベル３） | [7 empty] | 169767 | 149556 | 131991 | 130235 | 120310 | 103828 | 86297 | 68892
|  | Ａ | ｂ | Level 1 | Ab1 | 7 | 1191.4224 | 1537.4717 | 1352.3276 | 1191.4224 | 1175.3364 | 1084.4179 | 933.4335 | 772.8398 | 613.4002 | [6 empty] | レベル１ | 1.1 | [6 empty] | Ａ | ｂ | 169767 | 149556 | 131991 | 130235 | 120310 | 103828 | 86297 | 68892
|  |  |  | Level 2 | Ab2 | 8 | 1099.1922 | 1413.7825 | 1245.4697 | 1099.1922 | 1084.5686 | 1001.9154 | 864.6569 | 718.6626 | 573.7175 | [6 empty] | レベル２ | 1 | [6 empty] | 住戸全体 | 居室間歇 | 169767 | 149556 | 131991 | 130235 | 120310 | 103828 | 86297 | 68892
|  |  |  | Level 4 | Ab4 | 9 | 914.7318 | 1166.4041 | 1031.7538 | 914.7318 | 903.033 | 836.9104 | 727.1036 | 610.3081 | 494.3521 | [6 empty] | レベル４ | 0.8 | [6 empty] | ダクトセントラル | ルームエアコン | 169767 | 149556 | 131991 | 130235 | 120310 | 103828 | 86297 | 68892
|  |  |  | Reference | Ba0 | 10 | 883.5276 | 999.567 | 943.7125 | 883.5276 | 902.1153 | 843.3628 | 828.3228 | 750.6496 | 853.2895 | [16 empty] | 120028 | 113321 | 106094 | 108326 | 101271 | 99465 | 90138 | 102463
|  | Ｂ | ａ | Level 1 | Ba1 | 11 | 954.1914 | 1081.8346 | 1020.3947 | 954.1914 | 974.6377 | 910.01 | 893.466 | 808.0255 | 920.9294 | [14 empty] | Ｂ | ａ | 120028 | 113321 | 106094 | 108326 | 101271 | 99465 | 90138 | 102463
|  |  |  | Level 2 | Ba2 | 12 | 883.5276 | 999.567 | 943.7125 | 883.5276 | 902.1153 | 843.3628 | 828.3228 | 750.6496 | 853.2895 | [14 empty] | 居室連続 | 住戸全体 | 120028 | 113321 | 106094 | 108326 | 101271 | 99465 | 90138 | 102463
|  |  |  | Level 4 | Ba4 | 13 | 742.2002 | 835.0316 | 790.3481 | 742.2002 | 757.0703 | 710.0683 | 698.0363 | 635.8977 | 718.0097 | [14 empty] | パネルラジエーター | ダクトセントラル | 120028 | 113321 | 106094 | 108326 | 101271 | 99465 | 90138 | 102463
|  |  |  | Reference | Bb0 | 14 | 862.9664 | 985.9427 | 931.1709 | 862.9664 | 866.439 | 808.9107 | 752.2152 | 651.9654 | 573.7175 | [16 empty] | 118392 | 111815 | 103625 | 104042 | 97134 | 90326 | 78288 | 68892
|  | Ｂ | ｂ | Level 1 | Bb1 | 15 | 931.574 | 1066.8479 | 1006.5989 | 931.574 | 935.3939 | 872.1128 | 809.7477 | 699.4729 | 613.4002 | [14 empty] | Ｂ | ｂ | 118392 | 111815 | 103625 | 104042 | 97134 | 90326 | 78288 | 68892
|  |  |  | Level 2 | Bb2 | 16 | 862.9664 | 985.9427 | 931.1709 | 862.9664 | 866.439 | 808.9107 | 752.2152 | 651.9654 | 573.7175 | [14 empty] | 居室連続 | 居室間歇 | 118392 | 111815 | 103625 | 104042 | 97134 | 90326 | 78288 | 68892
|  |  |  | Level 4 | Bb4 | 17 | 725.7512 | 824.1322 | 780.3148 | 725.7512 | 728.5293 | 682.5067 | 637.1502 | 556.9504 | 494.3521 | [14 empty] | パネルラジエーター | ルームエアコン | 118392 | 111815 | 103625 | 104042 | 97134 | 90326 | 78288 | 68892
|  |  |  | Reference | Ca0 | 18 | 823.0929 | 937.2585 | 884.2522 | 823.0929 | 831.8871 | 745.1782 | 747.7682 | 705.6129 | 853.2895 | [16 empty] | 112546 | 106181 | 98837 | 99893 | 89481 | 89792 | 84730 | 102463
|  | Ｃ | ａ | Level 1 | Ca1 | 19 | 887.7132 | 1013.2953 | 954.9883 | 887.7132 | 897.3867 | 802.007 | 804.8559 | 758.4852 | 920.9294 | [14 empty] | Ｃ | ａ | 112546 | 106181 | 98837 | 99893 | 89481 | 89792 | 84730 | 102463
|  |  |  | Level 2 | Ca2 | 20 | 823.0929 | 937.2585 | 884.2522 | 823.0929 | 831.8871 | 745.1782 | 747.7682 | 705.6129 | 853.2895 | [14 empty] | 居室間歇 | 住戸全体 | 112546 | 106181 | 98837 | 99893 | 89481 | 89792 | 84730 | 102463
|  |  |  | Level 4 | Ca4 | 21 | 693.8524 | 785.1849 | 742.7798 | 693.8524 | 700.8877 | 631.5207 | 633.5926 | 599.8684 | 718.0097 | [14 empty] | ルームエアコン | ダクトセントラル | 112546 | 106181 | 98837 | 99893 | 89481 | 89792 | 84730 | 102463
|  |  |  | Reference | Cb0 | 22 | 802.5233 | 923.6342 | 871.7022 | 802.5233 | 796.2109 | 710.7179 | 671.6606 | 606.937 | 573.7175 | [16 empty] | 110910 | 104674 | 96367 | 95609 | 85343 | 80653 | 72881 | 68892
|  | Ｃ | ｂ | Level 1 | Cb1 | 23 | 865.0866 | 998.3086 | 941.1834 | 865.0866 | 858.1429 | 764.1006 | 721.1376 | 649.9417 | 613.4002 | [14 empty] | Ｃ | ｂ | 110910 | 104674 | 96367 | 95609 | 85343 | 80653 | 72881 | 68892
|  |  |  | Level 2 | Cb2 | 24 | 802.5233 | 923.6342 | 871.7022 | 802.5233 | 796.2109 | 710.7179 | 671.6606 | 606.937 | 573.7175 | [14 empty] | 居室間歇 | 居室間歇 | 110910 | 104674 | 96367 | 95609 | 85343 | 80653 | 72881 | 68892
|  |  |  | Level 4 | Cb4 | 25 | 677.3967 | 774.2855 | 732.7398 | 677.3967 | 672.3468 | 603.9524 | 572.7065 | 520.9277 | 494.3521 |  |  |  | 暖房 | 冷房 | レベル | [8 empty] | ルームエアコン | ルームエアコン | 110910 | 104674 | 96367 | 95609 | 85343 | 80653 | 72881 | 68892
|  |  |  | Evaluated Building |  | 3: 1214.049; 8: *Energy consumption of ref. bld. (reference value) is equivalent to 0% in energy consumption reduction rate. |  |  |  | 0 | 0 | 0 | 000 | - | ←評価建物
|  |  |  | Reference Building |  | 3: 883.5276 | [6 empty] | 000 | - | ←参照値
d. Addition of GHG emissions related to equipment installation
|  | Equipment |  |  |  | 3: Construction stage; 3: Maintenance/Upgrade/Demolition stages *
[7 empty] | 30 | 60 | 90 | 30 | 60 | 90
|  | Solar power generation system |  |  |  |  | 38.68 | 19.34 | 12.89 | 39.1155 | 39.0067 | 38.9704 | kg-CO2eq/yr-kW
|  | Battery |  |  |  |  | 6.66 | 3.33 | 2.22 | 6.7172 | 6.7023 | 6.6973 | kg-CO2eq/yr-kWh
* Renewal intervals: 25 years (1 time for the evaluation period of 30 years, 2 times for 60 years, and 3 times for 90 years), Repair rate=0%, Waste related GHG is calculated based on the calculation method in J-CAT®
e. GHG calculation conditions
| Service life of building structure (years） |  |  |  |  | 3: S; 3: RC; 6: SRC
|  | Q2/2.2.1 Service Life of Structural Frame Materials |  |  |  |  | Level 3 | Level 4 | Level 5 | Level 3 | Level 4 | Level 5 | Level 3 | Level 4 | Level 5
|  |  | Office |  | 1 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  | School |  | 2 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  | Retailers |  | 3 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  |  | Restaurants |  | 4 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  |  | Halls |  | 5 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  | Factories |  | 6 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
|  |  | Hospitals |  | 7 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  | Hotels |  | 8 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  |  | Apartments |  | 9 |  | 30 | 60 | 90 | 30 | 60 | 90 | 30 | 60 | 90
| Quantities of Representative Materials | [5 empty] | No Reuse | Existing Structure 100% | Blast furnace cement100% | No Reuse | Existing Structure 100% | Blast furnace cement100% | No Reuse | Existing Structure 100% | Blast furnace cement100% |  |  |  |  | SRC | RC | S |  |  |  | 用途 | 構造 | コンクリート（m3/m2） | 型枠* | 鉄筋 | 鉄骨 | デッキプレート**
|  | Office | Regular concrete | m3/m2 |  |  | 0.567 | 0 | 0 | 0.772 | 0 | 0 | 0.696 | 0 | 0 |  |  | Office | Regular concrete | 0.696 | 0.772 | 0.567 |  | コンクリート（m3/m2）
|  |  | Blast furnace cement concrete | m3/m2 |  |  | 0 | 0 | 0.567 | 0 | 0 | 0.772 | 0 | 0 | 0.696 |  |  |  | Blast furnace cement concrete |  |  |  |  | 型枠* |  | ①集合住宅
|  |  | Formwork | m2/m2 |  |  | 0.4325 | 0 | 0.4325 | 1.05 | 0 | 1.05 | 0.6675 | 0 | 0.6675 |  |  |  | Formwork | 0.6675 | 1.05 | 0.4325 |  | 鉄筋 |  |  | SRC | 0.75 | 1.0425 | 0.136 | 0.052
|  |  | Reinforcing bars | t/m2 |  |  | 0.07 | 0 | 0.07 | 0.103 | 0 | 0.103 | 0.078 | 0 | 0.078 |  |  |  | Reinforcing bars | 0.078 | 0.103 | 0.07 |  | 鉄骨 |  |  | RC | 0.734 | 1.1075 | 0.1 | 0.012
|  |  | Steel frame | t/m2 |  |  | 0.136 | 0 | 0.136 | 0.038 | 0 | 0.038 | 0.1 | 0 | 0.1 |  |  |  | Steel frame | 0.1 | 0.038 | 0.136 |  | デッキプレート** |  |  | S | 0.323 | 0.165 | 0.019 | 0.048 | 1
|  |  | Deck plate | m2/m2 |  |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Deck plate |  |  | 1 |  |  |  | ②事務所
|  | School | Regular concrete | m3/m2 |  |  | 0.352 | 0 | 0 | 0.865 | 0 | 0 | 0.958 | 0 | 0 |  |  | School | Regular concrete | 0.958 | 0.865 | 0.352 |  |  |  |  | SRC | 0.696 | 0.6675 | 0.078 | 0.1
|  |  | Blast furnace cement concrete | m3/m2 |  |  | 0 | 0 | 0.352 | 0 | 0 | 0.865 | 0 | 0 | 0.958 |  |  |  | Blast furnace cement concrete | [7 empty] | RC | 0.772 | 1.05 | 0.103 | 0.038
|  |  | Formwork | m2/m2 |  |  | 0.17 | 0 | 0.17 | 1.225 | 0 | 1.225 | 0.9725 | 0 | 0.9725 |  |  |  | Formwork | 0.9725 | 1.225 | 0.17 |  |  |  |  | S | 0.567 | 0.4325 | 0.07 | 0.136 | 1
|  |  | Reinforcing bars | t/m2 |  |  | 0.045 | 0 | 0.045 | 0.112 | 0 | 0.112 | 0.11 | 0 | 0.11 |  |  |  | Reinforcing bars | 0.11 | 0.112 | 0.045 |  |  |  | ③小・中・高校
|  |  | Steel frame | t/m2 |  |  | 0.105 | 0 | 0.105 | 0.005 | 0 | 0.005 | 0.078 | 0 | 0.078 |  |  |  | Steel frame | 0.078 | 0.005 | 0.105 |  |  |  |  | SRC | 0.958 | 0.9725 | 0.11 | 0.078
|  |  | Deck plate | m2/m2 |  |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Deck plate |  |  | 1 |  |  |  |  | RC | 0.865 | 1.225 | 0.112 | 0.005
|  | Retailers | Regular concrete | m3/m2 |  |  | 0.342 | 0 | 0 | 0.912 | 0 | 0 | 0.307 | 0 | 0 |  |  | Retailers | Regular concrete | 0.307 | 0.912 | 0.342 |  |  |  |  | S | 0.352 | 0.17 | 0.045 | 0.105 | 1
|  |  | Blast furnace cement concrete | m3/m2 |  |  | 0 | 0 | 0.342 | 0 | 0 | 0.912 | 0 | 0 | 0.307 |  |  |  | Blast furnace cement concrete | [6 empty] | ④医療
|  |  | Formwork | m2/m2 |  |  | 0.155 | 0 | 0.155 | 1.435 | 0 | 1.435 | 0.4025 | 0 | 0.4025 |  |  |  | Formwork | 0.4025 | 1.435 | 0.155 |  |  |  | ・福祉施設 | SRC | 0.812 | 0.8075 | 0.089 | 0.066
|  |  | Reinforcing bars | t/m2 |  |  | 0.024 | 0 | 0.024 | 0.133 | 0 | 0.133 | 0.053 | 0 | 0.053 |  |  |  | Reinforcing bars | 0.053 | 0.133 | 0.024 |  |  |  |  | RC | 0.766 | 1.12 | 0.096 | 0.012
|  |  | Steel frame | t/m2 |  |  | 0.072 | 0 | 0.072 | - | 0 | - | 0.071 | 0 | 0.071 |  |  |  | Steel frame | 0.071 | - | 0.072 |  |  |  |  | S | 0.317 | 0.17 | 0.034 | 0.074 | 1
|  |  | Deck plate | m2/m2 |  |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Deck plate |  |  | 1 |  |  |  | ⑥飲食・店舗
|  | Restaurants | Regular concrete | m3/m2 |  |  | 0.342 | 0 | 0 | 0.912 | 0 | 0 | 0.307 | 0 | 0 |  |  | Restaurants | Regular concrete | 0.307 | 0.912 | 0.342 |  |  |  | ・量販店 | SRC | 0.307 | 0.4025 | 0.053 | 0.071
|  |  | Blast furnace cement concrete | m3/m2 |  |  | 0 | 0 | 0.342 | 0 | 0 | 0.912 | 0 | 0 | 0.307 |  |  |  | Blast furnace cement concrete | 0 | 0 | 0 |  |  |  |  | RC | 0.912 | 1.435 | 0.133 | -
|  |  | Formwork | m2/m2 |  |  | 0.155 | 0 | 0.155 | 1.435 | 0 | 1.435 | 0.4025 | 0 | 0.4025 |  |  |  | Formwork | 0.4025 | 1.435 | 0.155 |  |  |  |  | S | 0.342 | 0.155 | 0.024 | 0.072 | 1
|  |  | Reinforcing bars | t/m2 |  |  | 0.024 | 0 | 0.024 | 0.133 | 0 | 0.133 | 0.053 | 0 | 0.053 |  |  |  | Reinforcing bars | 0.053 | 0.133 | 0.024 |  |  |  | ⑦ホテル・旅館
|  |  | Steel frame | t/m2 |  |  | 0.072 | 0 | 0.072 | - | 0 | - | 0.071 | 0 | 0.071 |  |  |  | Steel frame | 0.071 | - | 0.072 |  |  |  |  | SRC | 0.816 | 1.04 | 0.093 | 0.084
|  |  | Deck plate | m2/m2 |  |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Deck plate | 0 | 0 | 1 |  |  |  |  | RC | 0.999 | 1.195 | 0.111 | 0.004
|  | Halls | Regular concrete | m3/m2 |  |  | 0.345 | 0 | 0 | 0.888 | 0 | 0 | 0.862 | 0 | 0 |  |  | Halls | Regular concrete | 0.862 | 0.888 | 0.345 |  |  |  |  | S | 0.436 | 0.3925 | 0.034 | 0.103 | 1
|  |  | Blast furnace cement concrete | m3/m2 |  |  | 0 | 0 | 0.345 | 0 | 0 | 0.888 | 0 | 0 | 0.862 |  |  |  | Blast furnace cement concrete | [6 empty] | ⑧体育館・講堂・
|  |  | Formwork | m2/m2 |  |  | 0.3625 | 0 | 0.3625 | 1.235 | 0 | 1.235 | 1.0225 | 0 | 1.0225 |  |  |  | Formwork | 1.0225 | 1.235 | 0.3625 |  |  |  | 集会施設 | SRC | 0.862 | 1.0225 | 0.1 | 0.059
|  |  | Reinforcing bars | t/m2 |  |  | 0.04 | 0 | 0.04 | 0.118 | 0 | 0.118 | 0.1 | 0 | 0.1 |  |  |  | Reinforcing bars | 0.1 | 0.118 | 0.04 |  |  |  |  | RC | 0.888 | 1.235 | 0.118 | 0.017
|  |  | Steel frame | t/m2 |  |  | 0.139 | 0 | 0.139 | 0.017 | 0 | 0.017 | 0.059 | 0 | 0.059 |  |  |  | Steel frame | 0.059 | 0.017 | 0.139 |  |  |  |  | S | 0.345 | 0.3625 | 0.04 | 0.139 | 1
|  |  | Deck plate | m2/m2 |  |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Deck plate |  |  | 1 |  |  |  | ⑨倉庫
|  | Factories | Regular concrete | m3/m2 |  |  | 0.354 | 0 | 0 | 0.77 | 0 | 0 | 0.669 | 0 | 0 |  |  | Factories | Regular concrete | 0.669 | 0.77 | 0.354 |  |  |  | ・流通施設 | SRC | 0.669 | 0.5575 | 0.08 | 0.077
|  |  | Blast furnace cement concrete | m3/m2 |  |  | 0 | 0 | 0.354 | 0 | 0 | 0.77 | 0 | 0 | 0.669 |  |  |  | Blast furnace cement concrete | [7 empty] | RC | 0.77 | 0.7625 | 0.108 | 0.01
|  |  | Formwork | m2/m2 |  |  | 0.175 | 0 | 0.175 | 0.7625 | 0 | 0.7625 | 0.5575 | 0 | 0.5575 |  |  |  | Formwork | 0.5575 | 0.7625 | 0.175 |  |  |  |  | S | 0.354 | 0.175 | 0.031 | 0.088 | 1
|  |  | Reinforcing bars | t/m2 |  |  | 0.031 | 0 | 0.031 | 0.108 | 0 | 0.108 | 0.08 | 0 | 0.08 |  |  |  | Reinforcing bars | 0.08 | 0.108 | 0.031
|  |  | Steel frame | t/m2 |  |  | 0.088 | 0 | 0.088 | 0.01 | 0 | 0.01 | 0.077 | 0 | 0.077 |  |  |  | Steel frame | 0.077 | 0.01 | 0.088
|  |  | Deck plate | m2/m2 |  |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Deck plate |  |  | 1
|  | Hospitals | Regular concrete | m3/m2 |  |  | 0.317 | 0 | 0 | 0.766 | 0 | 0 | 0.812 | 0 | 0 |  |  | Hospitals | Regular concrete | 0.812 | 0.766 | 0.317
|  |  | Blast furnace cement concrete | m3/m2 |  |  | 0 | 0 | 0.317 | 0 | 0 | 0.766 | 0 | 0 | 0.812 |  |  |  | Blast furnace cement concrete
|  |  | Formwork | m2/m2 |  |  | 0.17 | 0 | 0.17 | 1.12 | 0 | 1.12 | 0.8075 | 0 | 0.8075 |  |  |  | Formwork | 0.8075 | 1.12 | 0.17
|  |  | Reinforcing bars | t/m2 |  |  | 0.034 | 0 | 0.034 | 0.096 | 0 | 0.096 | 0.089 | 0 | 0.089 |  |  |  | Reinforcing bars | 0.089 | 0.096 | 0.034
|  |  | Steel frame | t/m2 |  |  | 0.074 | 0 | 0.074 | 0.012 | 0 | 0.012 | 0.066 | 0 | 0.066 |  |  |  | Steel frame | 0.066 | 0.012 | 0.074
|  |  | Deck plate | m2/m2 |  |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Deck plate |  |  | 1
|  | Hotels | Regular concrete | m3/m2 |  |  | 0.436 | 0 | 0 | 0.999 | 0 | 0 | 0.816 | 0 | 0 |  |  | Hotels | Regular concrete | 0.816 | 0.999 | 0.436
|  |  | Blast furnace cement concrete | m3/m2 |  |  | 0 | 0 | 0.436 | 0 | 0 | 0.999 | 0 | 0 | 0.816 |  |  |  | Blast furnace cement concrete
|  |  | Formwork | m2/m2 |  |  | 0.3925 | 0 | 0.3925 | 1.195 | 0 | 1.195 | 1.04 | 0 | 1.04 |  |  |  | Formwork | 1.04 | 1.195 | 0.3925
|  |  | Reinforcing bars | t/m2 |  |  | 0.034 | 0 | 0.034 | 0.111 | 0 | 0.111 | 0.093 | 0 | 0.093 |  |  |  | Reinforcing bars | 0.093 | 0.111 | 0.034
|  |  | Steel frame | t/m2 |  |  | 0.103 | 0 | 0.103 | 0.004 | 0 | 0.004 | 0.084 | 0 | 0.084 |  |  |  | Steel frame | 0.084 | 0.004 | 0.103
|  |  | Deck plate | m2/m2 |  |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Deck plate |  |  | 1
|  | Apartments | Regular concrete | m3/m2 |  |  | 0.323 | 0 | 0 | 0.734 | 0 | 0 | 0.75 | 0 | 0 |  |  | Apartments | Regular concrete | 0.75 | 0.734 | 0.323
|  |  | Blast furnace cement concrete | m3/m2 |  |  | 0 | 0 | 0.323 | 0 | 0 | 0.734 | 0 | 0 | 0.75 |  |  |  | Blast furnace cement concrete
|  |  | Formwork | m2/m2 |  |  | 0.165 | 0 | 0.165 | 1.1075 | 0 | 1.1075 | 1.0425 | 0 | 1.0425 |  |  |  | Formwork | 1.0425 | 1.1075 | 0.165
|  |  | Reinforcing bars | t/m2 |  |  | 0.019 | 0 | 0.019 | 0.1 | 0 | 0.1 | 0.136 | 0 | 0.136 |  |  |  | Reinforcing bars | 0.136 | 0.1 | 0.019
|  |  | Steel frame | t/m2 |  |  | 0.048 | 0 | 0.048 | 0.012 | 0 | 0.012 | 0.052 | 0 | 0.052 |  |  |  | Steel frame | 0.052 | 0.012 | 0.048
|  |  | Deck plate | m2/m2 |  |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Deck plate |  |  | 1
Renewal interval (years)
|  | Exterior |  |  |  |  | S Level 3: 25; S Level 4: years
Roof
|  | Interior |  |  |  |  | S Level 3: 18; S Level 4: years
|  | Building Service |  |  |  |  | S Level 3: 15; S Level 4: years
Repair rate
|  | Exterior |  |  |  |  | S Level 3: 1%; S Level 4: /yr
|  | Interior |  |  |  |  | S Level 3: 1%; S Level 4: /yr
|  | Building Service |  |  |  |  | S Level 3: 2%; S Level 4: /yr

## Weight
n Weighting coefficients | [11 empty] | Weighting coefficients(default)
[12 empty] | 2 | CASBEE | NC | [13 empty] | 0. 既存 | [15 empty] | １．基本設計 | [15 empty] | ２．実施・竣工段階 | [16 empty] | ３．短期使用 | [15 empty] | ４．ｲﾝﾃﾘｱｽﾍﾟｰｽ
|  | After correction |  | Before correction |  | Total (Before correction) |  | Selection of "Excluded" |  | Weighting coefficients (default) |  |  |  |  | Entire Building and Common areas | [8 empty] | ES/JS/JHS | Dwelling and Accommodation areas | [5 empty] | 建物全体・共用部 | [8 empty] | 小中高 | 住居・宿泊部 | [5 empty] | 建物全体・共用部 | [8 empty] | 小中高 | 住居・宿泊部 | [5 empty] | 建物全体・共用部 | [8 empty] | 小中高 | 住居・宿泊部 | [6 empty] | 建物全体・共用部 | [8 empty] | 小中高 | 住居・宿泊部 | [5 empty] | 建物全体・共用部 | [8 empty] | 小中高 | 住居・宿泊部
|  | Entire Building and Common | Dwelling and Accommodation | Entire Building and Common | Dwelling and Accommodation | Entire Building and Common | Dwelling and Accommodation | Entire Building and Common | Dwelling and Accommodation | Entire Building and Common | Dwelling and Accommodation |  |  | Name of assessment item | Off | Sch | Rtl | Rst | Hsp | Htl | Apt | Hal | Fct | Sch | Hsp-o | Htl-o | Apt-o |  | 項目 | 項目名 | 事務所 | 学校 | 物販店 | 飲食店 | 病院 | ホテル | 集合住宅 | 集会所 | 工場 | 学校 | 病院o | ホテルo | 集合住宅o |  | 項目 | 項目名 | 事務所 | 学校 | 物販店 | 飲食店 | 病院 | ホテル | 集合住宅 | 集会所 | 工場 | 学校 | 病院o | ホテルo | 集合住宅o |  | 項目 | 項目名 | 事務所 | 学校 | 物販店 | 飲食店 | 病院 | ホテル | 集合住宅 | 集会所 | 工場 | 学校 | 病院o | ホテルo | 集合住宅o |  |  | 項目 | 項目名 | 事務所 | 学校 | 物販店 | 飲食店 | 病院 | ホテル | 集合住宅 | 集会所 | 工場 | 学校 | 病院o | ホテルo | 集合住宅o |  | 項目 | 項目名 | 事務所 | 学校 | 物販店 | 飲食店 | 病院 | ホテル | 集合住宅 | 集会所 | 工場 | 学校 | 病院o | ホテルo | 集合住宅o
| Area ratio by building type | 1 | 0 | [10 empty] | Area ratio by building type | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Q | Environmental Quality of Building |  |  |  |  | 1 | 0 | [5 empty] | Q | Ratio of Residential & Accommodation Section | [10 empty] | 0 | 0 | 0 | Q |  | 建築物の環境品質 | [13 empty] | Q |  | 建築物の環境品質 | [13 empty] | Q |  | Environmental Quality of Building | [14 empty] | Q |  | 建築物の環境品質 | [13 empty] | Q |  | 建築物の環境品質 | 0 | bar: Entire Building and Common areas Off to ES/JS/JHS Sch
Q1 | Indoor Environment | 0.4 | 0 | 0.4 | 0 | 1 | 0 | 1 |  | 0.4 | 0 | Q1 | Q | Indoor Environment | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 | 0 | 0 | 0 | Q1 | Q | 室内環境 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 |  |  |  | Q1 | Q | 室内環境 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 |  |  |  | Q1 | Q | Indoor Environment | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 |  |  |  |  | Q1 | Q | 室内環境 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.5 | 0 | 0 | 0 | Q1 | Q | 室内環境 | 0.5
1 | Sound Environment | 0.15 | 0 | 0.15 | 0 | 1 | 0 | 1 | 0 | 0.15 | 0 | 1 | Q1 | Sound Environment | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 1 | Q1 | 音環境 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.23 | 0.15 | 0.15 |  |  |  | 1 | Q1 | 音環境 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.23 | 0.15 | 0.15 |  |  |  | 1 | Q1 | Sound Environment | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 |  |  |  |  | 1 | Q1 | 音環境 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 1 | Q1 | 音環境 | 0.15
1.1 | Indoor Noise Level | 0.4 | 0 | 0.4 | 0 | 0 | 0 | 1 | 1 | 0.4 | 0 | 1.1 | Q1 1 | Indoor Noise Level | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 1.1 | Q1 1 | 騒音 | 0.4 | 0.4 | 0.8 | 0.4 | 0.4 | 0.8 | 0.8 | 0.8 | 0.5 | 0.4 | 0.5 | 0.4 | 0.4 | 1.1 | Q1 1 | 騒音 | [7 empty] | 0.4 | [5 empty] | 1.1 | Q1 1 | Indoor Noise Level | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 |  | 1.1 | Q1 1 | 室内騒音レベル | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | Q1 1 | 室内騒音レベル | 1
1.1.1 | Background noise level | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 1.1.1 | Q1 1.1 | Background noise level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1.1 | Q1 1.1 | 室内騒音レベル | 0.4 | 1 | 1 | 1 | 0.4 | 1 | 1 | 1 | 0.4 | 1 | 0.4 | 1 | 1 | 1.1.1 | Q1 1.1 | 室内騒音レベル | [7 empty] | 1 | [5 empty] | 1.1.1 | Q1 1.1 | Background noise level | [14 empty] | 1.1.1 | Q1 1.1 | [14 empty] | 1.1.1 | Q1 1.1 |  | 0
1.1.2 | Equipment noise | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 1.1.2 | Q1 1.1 | Equipment noise | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1.2 | Q1 1.1 | 設備騒音対策 | 0.6 |  |  |  | 0.6 |  |  |  | 0.6 |  | 0.6 |  |  | 1.1.2 | Q1 1.1 | 設備騒音対策 | [13 empty] | 1.1.2 | Q1 1.1 | Equipment noise | [14 empty] | 1.1.2 | Q1 1.1 | [14 empty] | 1.1.2 | Q1 1.1 |  | 0
1.2 | Sound Insulation | 0.4 | 0 | 0.4 | 0 | 1 | 0 | 1 | 0 | 0.4 | 0 | 1.2 | Q1 1 | Sound Insulation | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 1.2 | Q1 1 | 遮音 | 0.4 | 0.4 |  | 0.4 | 0.4 |  |  |  | 0.5 | 0.4 | 0.5 | 0.4 | 0.4 | 1.2 | Q1 1 | 遮音 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 0.4 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1.2 | Q1 1 | Sound Insulation | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 |  | 1.2 | Q1 1 | 遮音 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 1 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 1 | 1.2 | Q1 1 | 遮音 | 0
1.2.1 | Sound Insulation of Openings | 0.6 | 0 | 0.6 | 0 |  |  | 1 | 0 | 0.6 | 0 | 1.2.1 | Q1 1.2 | Sound Insulation of Openings | 0.6 | 0.3 | 1 | 0.6 | 0.4 | 1 | 1 | 1 | 0.6 | 0.3 | 0.3 | 0.3 | 0.3 | 1.2.1 | Q1 1.2 | 開口部遮音性能 | [13 empty] | 1.2.1 | Q1 1.2 | 開口部遮音性能 | 0.6 | 0.4 | 1 | 0.6 | 0.4 | 1 | 1 | 1 | 0.6 | 0.4 | 0.3 | 0.3 | 0.3 | 1.2.1 | Q1 1.2 | Sound Insulation of Openings | 0.6 | 0.3 | 1 | 0.6 | 0.4 | 1 | 1 | 1 | 0.6 | 0.3 | 0.3 | 0.3 | 0.3 |  | 1.2.1 | Q1 1.2 | 開口部遮音性能 | 0.6 | 0.3 | 1 | 0.6 | 0.4 | 1 | 1 | 1 | 0.6 | 0.3 | 0.3 | 0.3 | 0.3 | 1.2.1 | Q1 1.2 | 開口部遮音性能 | 0
1.2.2 | Sound Insulation of Partition Walls | 0.4 | 0 | 0.4 | 0 |  |  | 1 | 1 | 0.4 | 0 | 1.2.2 | Q1 1.2 | Sound Insulation of Partition Walls | 0.4 | 0.3 | 0 | 0.4 | 0.6 | 0 | 0 | 0 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 1.2.2 | Q1 1.2 | 界壁遮音性能 | 1 | 0.4 |  | 1 | 0.4 |  |  |  | 1 | 0.4 | 1 | 0.4 | 0.4 | 1.2.2 | Q1 1.2 | 界壁遮音性能 | 0.4 | 0.3 |  | 0.4 | 0.6 |  |  |  | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 1.2.2 | Q1 1.2 | Sound Insulation of Partition Walls | 0.4 | 0.3 |  | 0.4 | 0.6 |  |  |  | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 |  | 1.2.2 | Q1 1.2 | 界壁遮音性能 | 0.4 | 0.3 | 0 | 0.4 | 0.6 | 0 | 0 | 0 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 1.2.2 | Q1 1.2 | 界壁遮音性能 | 0
1.2.3 | Sound Insulation Performance of Floor Slabs (light-weight impact source) | 0 | 0 | 0 | 0 |  |  | 1 | 1 | 0 | 0 | 1.2.3 | Q1 1.2 | Sound Insulation Performance of Floor Slabs (light-weight impact source) | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 1.2.3 | Q1 1.2 | 界床遮音性能（軽量衝撃源） |  | 0.3 |  |  | 0.6 |  |  |  |  | 0.3 |  | 0.3 | 0.3 | 1.2.3 | Q1 1.2 | 界床遮音性能（軽量衝撃源） |  | 0.15 | [7 empty] | 0.15 | 0.2 | 0.2 | 0.2 | 1.2.3 | Q1 1.2 | Sound Insulation Performance of Floor Slabs (light-weight impact source) |  | 0.2 | [7 empty] | 0.2 | 0.2 | 0.2 | 0.2 |  | 1.2.3 | Q1 1.2 | 界床遮音性能（軽量衝撃源） | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 1.2.3 | Q1 1.2 | 界床遮音性能（軽量衝撃源） | 0
1.2.4 | Sound Insulation Performance of Floor Slabs (heavy-weight impact source) | 0 | 0 | 0 | 0 |  |  | 1 | 1 | 0 | 0 | 1.2.4 | Q1 1.2 | Sound Insulation Performance of Floor Slabs (heavy-weight impact source) | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 1.2.4 | Q1 1.2 | 界床遮音性能（重量衝撃源） |  | 0.3 | [7 empty] | 0.3 |  | 0.3 | 0.3 | 1.2.4 | Q1 1.2 | 界床遮音性能（重量衝撃源） |  | 0.15 | [7 empty] | 0.15 | 0.2 | 0.2 | 0.2 | 1.2.4 | Q1 1.2 | Sound Insulation Performance of Floor Slabs (heavy-weight impact source) |  | 0.2 | [7 empty] | 0.2 | 0.2 | 0.2 | 0.2 |  | 1.2.4 | Q1 1.2 | 界床遮音性能（重量衝撃源） | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 1.2.4 | Q1 1.2 | 界床遮音性能（重量衝撃源） | 0
1.3 | Sound Absorption | 0.2 | 0 | 0.2 | 0 |  |  | 1 | 1 | 0.2 | 0 | 1.3 | Q1 1 | Sound Absorption | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 1.3 | Q1 1 | 吸音 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 1.3 | Q1 1 | 吸音 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 1.3 | Q1 1 | Sound Absorption | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 |  | 1.3 | Q1 1 | 吸音 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0 | 1.3 | Q1 1 | 吸音 | 0
2 | Thermal Comfort | 0.35 | 0 | 0.35 | 0 | 0.8 | 0 | 1 | 0 | 0.35 | 0 | 2 | Q1 | Thermal Comfort | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 2 | Q1 | 温熱環境 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.44 | 0.35 | 0.35 |  |  |  | 2 | Q1 | 温熱環境 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.44 | 0.35 | 0.35 |  |  |  | 2 | Q1 | Thermal Comfort | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 |  |  |  |  | 2 | Q1 | 温熱環境 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 2 | Q1 | 温熱環境 | 0.35
2.1 | Room Temperature Control | 0.625 | 0 | 0.5 | 0 | 1 | 0 | 1 | 0 | 0.5 | 0 | 2.1 | Q1 2 | Room Temperature Control | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 2.1 | Q1 2 | 室温制御 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 2.1 | Q1 2 | 室温制御 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 2.1 | Q1 2 | Room Temperature Control | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 2.1 | Q1 2 | 室温制御 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 2.1 | Q1 2 | 室温制御 | 0.5
2.1.1 | Room Temperature | 0.375 | 0 | 0.375 | 0 |  |  | 1 | 1 | 0.375 | 0 | 2.1.1 | Q1 2.1 | Room Temperature | 0.375 | 0.6 | 0.5 | 0.5 | 0.375 | 0.375 | 0.625 | 0.375 | 0.375 | 0.6 | 0.57143 | 0.57143 | 0.625 | 2.1.1 | Q1 2.1 | 室温設定 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.3 | 0.3 | 0.3 |  |  |  | 2.1.1 | Q1 2.1 | 室温 | 0.3 | 0.6 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.3 | 0.3 | 0.6 | 0.6 | 0.6 | 0.6 | 2.1.1 | Q1 2.1 | Room Temperature | 0.375 | 0.6 | 0.5 | 0.5 | 0.375 | 0.375 | 0.625 | 0.375 | 0.375 | 0.6 | 0.57143 | 0.57143 | 0.625 |  | 2.1.1 | Q1 2.1 | 室温 | 0.375 | 0.6 | 0.5 | 0.5 | 0.375 | 0.375 | 0.625 | 0.375 | 0.375 | 0.6 | 0.57143 | 0.57143 | 0.625 | 2.1.1 | Q1 2.1 | 室温 | 0.375
2.1.2 | Variable Loads and Following-up Control | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 2.1.2 | Q1 2.1 | Variable Loads and Following-up Control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1.2 | Q1 2.1 | 負荷変動・追従制御性 |  | 0.2 | 0.2 | 0.2 |  |  |  | 0.3 |  | 0.2 |  |  |  | 2.1.2 | Q1 2.1 | 負荷変動・追従制御性 | [13 empty] | 2.1.2 | Q1 2.1 | Variable Loads and Following-up Control | [14 empty] | 2.1.2 | Q1 2.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1.2 | Q1 2.1 |  | 0
2.1.2 | Perimeter Performance | 0.25 | 0 | 0.25 | 0 |  |  | 1 | 1 | 0.25 | 0 | 2.1.2 | Q1 2.1 | Perimeter Performance | 0.25 | 0.4 | 0.16667 | 0.16667 | 0.25 | 0.25 | 0.375 | 0.25 | 0.25 | 0.4 | 0.42857 | 0.42857 | 0.375 | 2.1.3 | Q1 2.1 | 外皮性能 | 0.2 | 0.2 | 0.1 | 0.1 | 0.2 | 0.2 | 0.3 | 0.1 | 0.2 | 0.2 | 0.5 | 0.5 | 0.6 | 2.1.3 | Q1 2.1 | 外皮性能 | 0.2 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 2.1.2 | Q1 2.1 | Perimeter Performance | 0.25 | 0.4 | 0.16667 | 0.16667 | 0.25 | 0.25 | 0.375 | 0.25 | 0.25 | 0.4 | 0.42857 | 0.42857 | 0.375 |  | 2.1.3 | Q1 2.1 | 外皮性能 | 0.25 | 0.4 | 0.16667 | 0.16667 | 0.25 | 0.25 | 0.375 | 0.25 | 0.25 | 0.4 | 0.42857 | 0.42857 | 0.375 | 2.1.3 | Q1 2.1 | 外皮性能 | 0.25
2.1.3 | Zoned Control | 0.375 | 0 | 0.375 | 0 |  |  | 1 | 0 | 0.375 | 0 | 2.1.3 | Q1 2.1 | Zoned Control | 0.375 | 0 | 0.33333 | 0.33333 | 0.375 | 0.375 | 0 | 0.375 | 0.375 | 0 | 0 | 0 | 0 | 2.1.4 | Q1 2.1 | ゾーン別制御性 | 0.3 |  | 0.2 | 0.2 | 0.3 | 0.3 |  | 0.2 | 0.3 | 0 |  |  |  | 2.1.4 | Q1 2.1 | ゾーン別制御性 | 0.5 |  | 0.5 | 0.5 | 0.5 | 0.5 |  | 0.5 | 0.5 |  |  |  |  | 2.1.3 | Q1 2.1 | Zoned Control | 0.375 |  | 0.33333 | 0.33333 | 0.375 | 0.375 |  | 0.375 | 0.375 | [5 empty] | 2.1.4 | Q1 2.1 | ゾーン別制御性 | 0.375 | 0 | 0.33333 | 0.33333 | 0.375 | 0.375 | 0 | 0.375 | 0.375 | 0 | 0 | 0 | 0 | 2.1.4 | Q1 2.1 | ゾーン別制御性 | 0.375
2.1.5 | Temperature and Humidity Control | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 2.1.5 | Q1 2.1 | Temperature and Humidity Control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1.5 | Q1 2.1 | 温度・湿度制御 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 |  | 2.1.5 | Q1 2.1 | 温度・湿度制御 | [13 empty] | 2.1.5 | Q1 2.1 | Temperature and Humidity Control | [14 empty] | 2.1.5 | Q1 2.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1.5 | Q1 2.1 |  | 0
2.1.6 | Individual Control | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 2.1.6 | Q1 2.1 | Individual Control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1.6 | Q1 2.1 | 個別制御 | [9 empty] | 0 | 0.2 | 0.2 | 0.4 | 2.1.6 | Q1 2.1 | 個別制御 | [13 empty] | 2.1.6 | Q1 2.1 | Individual Control | [14 empty] | 2.1.6 | Q1 2.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1.6 | Q1 2.1 |  | 0
2.1.7 | Allowance for After-hours Air Conditioning | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 2.1.7 | Q1 2.1 | Allowance for After-hours Air Conditioning | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1.7 | Q1 2.1 | 時間外空調に対する配慮 | 0.1 | 0.2 |  |  | 0.1 | 0.1 |  |  | 0.1 | 0.2 |  |  |  | 2.1.7 | Q1 2.1 | 時間外空調に対する配慮 | [13 empty] | 2.1.7 | Q1 2.1 | Allowance for After-hours Air Conditioning | [14 empty] | 2.1.7 | Q1 2.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1.7 | Q1 2.1 |  | 0
2.1.8 | Monitoring Systems | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 2.1.8 | Q1 2.1 | Monitoring Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1.8 | Q1 2.1 | 監視システム |  |  | 0.1 | 0.1 | [5 empty] | 0 |  |  |  | 2.1.8 | Q1 2.1 | 監視システム | [13 empty] | 2.1.8 | Q1 2.1 | Monitoring Systems | [14 empty] | 2.1.8 | Q1 2.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1.8 | Q1 2.1 |  | 0
2.2 | Humidity Control | 0 | 0 | 0 | 0 |  |  | 0 | 1 | 0.2 | 0 | 2.2 | Q1 2 | Humidity Control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 2.2 | Q1 2 | 湿度制御 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.2 | Q1 2 | 湿度制御 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 2.2 | Q1 2 | Humidity Control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 2.2 | Q1 2 | 湿度制御 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 2.2 | Q1 2 | 湿度制御 | 0.2
2.3 | Type of Air Conditioning System | 0.375 | 0 | 0.3 | 0 |  |  | 1 | 1 | 0.3 | 0 | 2.3 | Q1 2 | Type of Air Conditioning System | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.3 | Q1 2 | [14 empty] | 2.3 | Q1 2 | 空調方式 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.3 | Q1 2 | Type of Air Conditioning System | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  | 2.3 | Q1 2 | 空調方式 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.3 | Q1 2 | 空調方式 | 0.3
2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | Q1 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | Q1 2 | 空調方式（既存） | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 2.3 | Q1 2 | 空調方式 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 2.3 | Q1 2 | [15 empty] | 2.3 | Q1 2 | [14 empty] | 2.3 | Q1 2 |  | 0
2.3.1 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 2.3.1 | Q1 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3.1 | Q1 2.3 | 上下温度差 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 2.3.1 | Q1 2.3 | 上下温度差 | [13 empty] | 2.3.1 | Q1 2.3 | [8 empty] | 0 | [6 empty] | 2.3.1 | Q1 2.3 | [14 empty] | 2.3.1 | Q1 2.3 |  | 0
2.3.2 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 2.3.2 | Q1 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3.2 | Q1 2.3 | 平均気流速度 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 2.3.2 | Q1 2.3 | 平均気流速度 | [13 empty] | 2.3.2 | Q1 2.3 | [8 empty] | 0 | [6 empty] | 2.3.2 | Q1 2.3 | [14 empty] | 2.3.2 | Q1 2.3 |  | 0
3 | Lighting & Illumination | 0.25 | 0 | 0.25 | 0 | 1 | 0 | 1 | 0 | 0.25 | 0 | 3 | Q1 | Lighting & Illumination | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 3 | Q1 | 光・視環境 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0.25 | 0.25 |  |  |  | 3 | Q1 | 光・視環境 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  | 0.25 | 0.25 |  |  |  | 3 | Q1 | Lighting & Illumination | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  |  | 3 | Q1 | 光・視環境 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 3 | Q1 | 光・視環境 | 0.25
3.1 | Daylighting | 0.3 | 0 | 0.3 | 0 | 1 | 0 | 1 | 0 | 0.3 | 0 | 3.1 | Q1 3 | Daylighting | 0.3 | 0.3 | 0.5 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 3.1 | Q1 3 | 昼光利用 | 0.3 | 0.3 | 0.5 | 1 | 0.3 | 0.3 | 0.3 |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 3.1 | Q1 3 | 昼光利用 | 0.3 | 0.3 | 0.5 | 1 | 0.3 | 0.3 | 0.3 |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 3.1 | Q1 3 | Daylighting | 0.3 | 0.3 | 0.5 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  | 3.1 | Q1 3 | 昼光利用 | 0.3 | 0.3 | 0.5 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 3.1 | Q1 3 | 昼光利用 | 0.3
3.1.1 | Daylight Factor | 0.6 | 0 | 0.6 | 0 |  |  | 1 | 1 | 0.6 | 0 | 3.1.1 | Q1 3.1 | Daylight Factor | 0.6 | 0.6 | 0 | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 3.1.1 | Q1 3.1 | 昼光率 | 0.6 | 0.6 |  |  | 0.6 | 0.6 | 0.6 |  | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 3.1.1 | Q1 3.1 | 昼光率 | 0.6 | 0.6 |  |  | 0.6 | 0.6 | 0.6 |  | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 3.1.1 | Q1 3.1 | Daylight Factor | 0.6 | 0.6 |  |  | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 |  | 3.1.1 | Q1 3.1 | 昼光率 | 0.6 | 0.6 | 0 | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 3.1.1 | Q1 3.1 | 昼光率 | 0.6
3.1.2 | Openings by Orientation | 0 | 0 | 0 | 0 |  |  | 0 | 1 | 0 | 0 | 3.1.2 | Q1 3.1 | Openings by Orientation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 3.1.2 | Q1 3.1 | 方位別開口 | [12 empty] | 0.3 | 3.1.2 | Q1 3.1 | 方位別開口 | [12 empty] | 0.3 | 3.1.2 | Q1 3.1 | Openings by Orientation | [12 empty] | 0.3 |  | 3.1.2 | Q1 3.1 | 方位別開口 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 3.1.2 | Q1 3.1 | 方位別開口 | 0
3.1.3 | Daylight Devices | 0.4 | 0 | 0.4 | 0 |  |  | 1 | 1 | 0.4 | 0 | 3.1.3 | Q1 3.1 | Daylight Devices | 0.4 | 0.4 | 1 | 1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 3.1.3 | Q1 3.1 | 昼光利用設備 | 0.4 | 0.4 | 1 | 1 | 0.4 | 0.4 | 0.4 |  | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 3.1.3 | Q1 3.1 | 昼光利用設備 | 0.4 | 0.4 | 1 | 1 | 0.4 | 0.4 | 0.4 |  | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 3.1.3 | Q1 3.1 | Daylight Devices | 0.4 | 0.4 | 1 | 1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 |  | 3.1.3 | Q1 3.1 | 昼光利用設備 | 0.4 | 0.4 | 1 | 1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 3.1.3 | Q1 3.1 | 昼光利用設備 | 0.4
3.2 | Anti-glare Measures | 0.3 | 0 | 0.3 | 0 | 1 | 0 | 1 | 0 | 0.3 | 0 | 3.2 | Q1 3 | Anti-glare Measures | 0.3 | 0.3 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 3.2 | Q1 3 | グレア対策 | 0.3 | 0.3 |  |  | 0.3 | 0.3 | 0.3 |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 3.2 | Q1 3 | グレア対策 | 0.3 | 0.3 |  |  | 0.3 | 0.3 | 0.3 |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 3.2 | Q1 3 | Anti-glare Measures | 0.3 | 0.3 |  |  | 0.3 | 0.3 | 0.3 |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  | 3.2 | Q1 3 | グレア対策 | 0.3 | 0.3 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 3.2 | Q1 3 | グレア対策 | 0.3
3.2.1 | Glare from Light Fixtures | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 3.2.1 | Q1 3.2 | Glare from Light Fixtures | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2.1 | Q1 3.2 | 照明器具のグレア | 0.4 | 0.4 |  |  | 0.4 | 0.4 | 0.4 |  | 0.4 | 0.3 | 0.4 | 0.4 | 0.4 | 3.2.1 | Q1 3.2 | 照明器具のグレア | [13 empty] | 3.2.1 | Q1 3.2 | Glare from Light Fixtures | [14 empty] | 3.2.1 | Q1 3.2 | 照明器具のグレア | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2.1 | Q1 3.2 | 照明器具のグレア | 0
3.2.1 | Daylight Control | 1 | 0 | 1 | 0 |  |  | 1 | 1 | 1 | 0 | 3.2.1 | Q1 3.2 | Daylight Control | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 3.2.2 | Q1 3.2 | 昼光制御 | 0.6 | 0.6 |  |  | 0.6 | 0.6 | 0.6 |  | 0.6 | 0.4 | 0.6 | 0.6 | 0.6 | 3.2.2 | Q1 3.2 | 昼光制御 | 1 | 1 |  |  | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 1 | 3.2.1 | Q1 3.2 | Daylight Control | 1 | 1 |  |  | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 1 |  | 3.2.2 | Q1 3.2 | 昼光制御 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 3.2.2 | Q1 3.2 | 昼光制御 | 1
3.2.3 | Reflection Control | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 3.2.3 | Q1 3.3 | Reflection Control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2.3 | Q1 3.3 | 映り込み対策 | [9 empty] | 0.3 |  |  |  | 3.2.3 | Q1 3.3 | 映り込み対策 | [13 empty] | 3.2.3 | Q1 3.3 | Reflection Control | [14 empty] | 3.2.3 | Q1 3.3
3.3 | Illuminance Level | 0.15 | 0 | 0.15 | 0 | 0 | 0 | 1 | 1 | 0.15 | 0 | 3.3 | Q1 3 | Illuminance Level | 0.15 | 0.15 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 3.3 | Q1 3 | 照度 | 0.15 | 0.15 |  |  | 0.15 | 0.15 | 0.15 |  | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 3.3 | Q1 3 | 照度 | 0.15 | 0.15 |  |  | 0.15 | 0.15 | 0.15 |  | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 3.3 | Q1 3 | Illuminance Level | 0.15 | 0.15 |  |  | 0.15 | 0.15 | 0.15 | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 |  | 3.3 | Q1 3 | 照度 | 0.15 | 0.15 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 3.3 | Q1 3 | 照度 | 0.15
3.3.1 | 照度 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 3.3.1 | Q1 3.3 | 照度 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3.1 | Q1 3.3 | 照度 | [13 empty] | 3.3.1 | Q1 3.3 | 照度 | [13 empty] | 3.3.1 | Q1 3.3 | 照度 | [7 empty] | 0 | [6 empty] | 3.3.1 | Q1 3.3 | 照度 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3.1 | Q1 3.3 | 照度 | 0
3.3.2 | 照度均斉度 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 3.3.2 | Q1 3.3 | 照度均斉度 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3.2 | Q1 3.3 | 照度均斉度 | [13 empty] | 3.3.2 | Q1 3.3 | 照度均斉度 | [13 empty] | 3.3.2 | Q1 3.3 | 照度均斉度 | [7 empty] | 0 | [6 empty] | 3.3.2 | Q1 3.3 | 照度均斉度 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3.2 | Q1 3.3 | 照度均斉度 | 0
3.4 | Lighting Controllability | 0.25 | 0 | 0.25 | 0 |  |  | 1 | 1 | 0.25 | 0 | 3.4 | Q1 3 | Lighting Controllability | 0.25 | 0.25 | 0.5 | 0 | 0.25 | 0.25 | 0.25 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 3.4 | Q1 3 | 照明制御 | 0.25 | 0.25 | 0.5 |  | 0.25 | 0.25 | 0.25 |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 3.4 | Q1 3 | 照明制御 | 0.25 | 0.25 | 0.5 | 0 | 0.25 | 0.25 | 0.25 |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 3.4 | Q1 3 | Lighting Controllability | 0.25 | 0.25 | 0.5 |  | 0.25 | 0.25 | 0.25 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  | 3.4 | Q1 3 | 照明制御 | 0.25 | 0.25 | 0.5 | 0 | 0.25 | 0.25 | 0.25 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 3.4 | Q1 3 | 照明制御 | 0.25
4 | Air Quality | 0.25 | 0 | 0.25 | 0 | 1 | 0 | 1 | 0 | 0.25 | 0 | 4 | Q1 | Air Quality | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 4 | Q1 | 空気質環境 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.33 | 0.25 | 0.25 |  |  |  | 4 | Q1 | 空気質環境 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.33 | 0.25 | 0.25 |  |  |  | 4 | Q1 | Air Quality | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  |  | 4 | Q1 | 空気質環境 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 4 | Q1 | 空気質環境 | 0.25
4.1 | Source Control | 0.5 | 0 | 0.5 | 0 | 1 | 0 | 1 | 0 | 0.5 | 0 | 4.1 | Q1 4 | Source Control | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 0.5 | 0.5 | 0.5 | 0.625 | 0.625 | 0.625 | 4.1 | Q1 4 | 発生源対策 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 0.5 | 0.5 | 0.5 | 0.625 | 0.625 | 0.625 | 4.1 | Q1 4 | 発生源対策 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 0.5 | 0.5 | 0.5 | 0.625 | 0.625 | 0.625 | 4.1 | Q1 4 | Source Control | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 0.5 | 0.5 | 0.5 | 0.625 | 0.625 | 0.625 |  | 4.1 | Q1 4 | 発生源対策 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 0.5 | 0.5 | 0.5 | 0.625 | 0.625 | 0.625 | 4.1 | Q1 4 | 発生源対策 | 0.5
4.1.1 | Chemical Pollutants | 1 | 0 | 1 | 0 |  |  | 1 | 1 | 1 | 0 | 4.1.1 | Q1 4.1 | Chemical Pollutants | [10 empty] | 1 | 1 | 1 | 4.1.1 | Q1 4.1 | 化学汚染物質 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.33 | 0.33 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 4.1.1 | Q1 4.1 | 化学汚染物質 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4.1.1 | Q1 4.1 | Chemical Pollutants | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 4.1.1 | Q1 4.1 | 化学汚染物質 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4.1.1 | Q1 4.1 | 化学汚染物質 | 1 | bar: Entire Building and Common areas Off to ES/JS/JHS Sch
4.1.2 | Asbestos | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 4.1.2 | Q1 4.1 | Asbestos | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1.2 | Q1 4.1 | アスベスト対策 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.33 | 0.33 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 4.1.2 | Q1 4.1 | アスベスト対策 | [13 empty] | 4.1.2 | Q1 4.1 | Asbestos | [14 empty] | 4.1.2 | Q1 4.1
4.1.3 | Mites, Mold etc. | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 4.1.3 | Q1 4.1 | Mites, Mold etc. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1.3 | Q1 4.1 |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.33 | 0.33 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 4.1.3 | Q1 4.1 | ダニ・カビ等 | [13 empty] | 4.1.3 | Q1 4.1 | Mites, Mold etc. | [14 empty] | 4.1.3 | Q1 4.1 | ダニ・カビ等 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1.3 | Q1 4.1 | ダニ・カビ等 | 0
4.1.4 | Legionella | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 4.1.4 | Q1 4.1 | Legionella | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1.4 | Q1 4.1 | レジオネラ対策 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 4.1.4 | Q1 4.1 | レジオネラ対策 | [13 empty] | 4.1.4 | Q1 4.1 | Legionella | [14 empty] | 4.1.4 | Q1 4.1 | レジオネラ対策 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1.4 | Q1 4.1 | レジオネラ対策 | 0
4.2 | Ventilation | 0.3 | 0 | 0.3 | 0 | 1 | 0 | 1 | 0 | 0.3 | 0 | 4.2 | Q1 4 | Ventilation | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.3 | 0.3 | 0.375 | 0.375 | 0.375 | 4.2 | Q1 4 | 換気 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.3 | 0.3 | 0.375 | 0.375 | 0.375 | 4.2 | Q1 4 | 換気 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.3 | 0.3 | 0.375 | 0.375 | 0.375 | 4.2 | Q1 4 | Ventilation | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.3 | 0.3 | 0.375 | 0.375 | 0.375 |  | 4.2 | Q1 4 | 換気 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.3 | 0.3 | 0.375 | 0.375 | 0.375 | 4.2 | Q1 4 | 換気 | 0.3
4.2.1 | Ventilation Rate | 0.33333 | 0 | 0.33333 | 0 |  |  | 1 | 1 | 0.33333 | 0 | 4.2.1 | Q1 4.2 | Ventilation Rate | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 4.2.1 | Q1 4.2 | 換気量 | 0.25 | 0.25 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  | 0.33333 | 0.25 | 0.25 | 0.25 | 0.25 |  | 4.2.1 | Q1 4.2 | 換気量 | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 4.2.1 | Q1 4.2 | Ventilation Rate | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  | 4.2.1 | Q1 4.2 | 換気量 | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 4.2.1 | Q1 4.2 | 換気量 | 0.33333
4.2.2 | Natural Ventilation Performance | 0.33333 | 0 | 0.33333 | 0 |  |  | 1 | 1 | 0.33333 | 0 | 4.2.2 | Q1 4.2 | Natural Ventilation Performance | 0.33333 | 0.33333 | 0 | 0 | 0 | 0 | 0 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 4.2.2 | Q1 4.2 | 自然換気性能 | 0.25 | 0.25 | [6 empty] | 0.25 | 0.25 | 0.25 | 0.25 | 0.33 | 4.2.2 | Q1 4.2 | 自然換気性能 | 0.33333 | 0.33333 | [6 empty] | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 4.2.2 | Q1 4.2 | Natural Ventilation Performance | 0.33333 | 0.33333 | [5 empty] | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  | 4.2.2 | Q1 4.2 | 自然換気性能 | 0.33333 | 0.33333 | 0 | 0 | 0 | 0 | 0 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 4.2.2 | Q1 4.2 | 自然換気性能 | 0.33333
4.2.3 | Consideration for Outside Air Intake | 0.33333 | 0 | 0.33333 | 0 |  |  | 1 | 1 | 0.33333 | 0 | 4.2.3 | Q1 4.2 | Consideration for Outside Air Intake | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 4.2.3 | Q1 4.2 | 取り入れ外気への配慮 | 0.25 | 0.25 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 1 | 0.33333 | 0.25 | 0.25 | 0.25 | 0.25 | 0.33 | 4.2.3 | Q1 4.2 | 取り入れ外気への配慮 | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 4.2.3 | Q1 4.2 | Consideration for Outside Air Intake | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  | 4.2.3 | Q1 4.2 | 取り入れ外気への配慮 | 0.33333 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 4.2.3 | Q1 4.2 | 取り入れ外気への配慮 | 0.33333
4.2.4 | Air Supply Planning | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 4.2.4 | Q1 4.2 | Air Supply Planning | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2.4 | Q1 4.2 | 給気計画 | 0.25 | 0.25 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  | 0.33333 | 0.25 | 0.25 | 0.25 | 0.25 | 0.33 | 4.2.4 | Q1 4.2 | 給気計画 | [13 empty] | 4.2.4 | Q1 4.2 | Air Supply Planning | [14 empty] | 4.2.4 | Q1 4.2
4.3 | Operation Plan | 0.2 | 0 | 0.2 | 0 | 1 | 0 | 1 | 0 | 0.2 | 0 | 4.3 | Q1 4 | Operation Plan | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 4.3 | Q1 4 | 運用管理 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 0.2 | 0.2 | 0.2 |  |  |  | 4.3 | Q1 4 | 運用管理 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 0.2 | 0.2 | 0.2 |  |  |  | 4.3 | Q1 4 | Operation Plan | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 0.2 | 0.2 | 0.2 |  |  |  |  | 4.3 | Q1 4 | 運用管理 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 4.3 | Q1 4 | 運用管理 | 0.2
4.3.1 | CO2 Monitoring | 0.5 | 0 | 0.5 | 0 |  |  | 1 | 0 | 0.5 | 0 | 4.3.1 | Q1 4.3 | CO2 Monitoring | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 4.3.1 | Q1 4.3 | CO2の監視 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 0.5 | 0.5 | 0.5 |  |  |  | 4.3.1 | Q1 4.3 | CO2の監視 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 0.5 | 0.5 | 0.5 |  |  |  | 4.3.1 | Q1 4.3 | CO2 Monitoring | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 0.5 | 0.5 | 0.5 |  |  |  |  | 4.3.1 | Q1 4.3 | CO2の監視 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 4.3.1 | Q1 4.3 | CO2の監視 | 0.5
4.3.2 | Control of Smoking | 0.5 | 0 | 0.5 | 0 |  |  | 1 | 0 | 0.5 | 0 | 4.3.2 | Q1 4.3 | Control of Smoking | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 0 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 4.3.2 | Q1 4.3 | 喫煙の制御 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 |  | 0.5 | 0.5 | 0.5 |  |  |  | 4.3.2 | Q1 4.3 | 喫煙の制御 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 |  | 0.5 | 0.5 | 0.5 |  |  |  | 4.3.2 | Q1 4.3 | Control of Smoking | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 |  | 0.5 | 0.5 | 0.5 |  |  |  |  | 4.3.2 | Q1 4.3 | 喫煙の制御 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 0 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 4.3.2 | Q1 4.3 | 喫煙の制御 | 0.5
Q2 | Quality of Service | 0.3 | 0 | 0.3 | 0 | 1 | 0 | 1 |  | 0.3 | 0 | Q2 | Q | Quality of Service | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | Q2 | Q | サービス性能 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | Q2 | Q | サービス性能 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | Q2 | Q | Quality of Service | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | Q2 | Q | サービス性能 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | Q2 | Q | サービス性能 | 0.4
1 | Service Ability | 0.4 | 0 | 0.4 | 0 | 1 | 0 | 1 | 0 | 0.4 | 0 | 1 | Q2 | Service Ability | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 1 | Q2 | 機能性 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | 1 | Q2 | 機能性 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | 1 | Q2 | Service Ability | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  |  | 1 | Q2 | 機能性 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0 | 0 | 0 | 1 | Q2 | 機能性 | 0.6
1.1 | Functionality & Usability | 0.4 | 0 | 0.4 | 0 | 1 | 0 | 1 | 0 | 0.4 | 0 | 1.1 | Q2 1 | Functionality & Usability | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 1.1 | Q2 1 | 機能性・使いやすさ | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 1.1 | Q2 1 | 機能性・使いやすさ | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 1.1 | Q2 1 | Functionality & Usability | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 |  | 1.1 | Q2 1 | 機能性・使いやすさ | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 1.1 | Q2 1 | 機能性・使いやすさ | 0.4
1.1.1 | Provision of Space & Storage | 0.33333 | 0 | 0.33333 | 0 |  |  | 1 | 1 | 0.33333 | 0 | 1.1.1 | Q2 1.1 | Provision of Space & Storage | 0.33333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33333 | 0 | 1 | 0.5 | 0 | 1.1.1 | Q2 1.1 | 広さ・収納性 | 0.33333 | [7 empty] | 0.33333 | 0.5 | 1 | 0.5 |  | 1.1.1 | Q2 1.1 | 広さ・収納性 | 0.33333 | [7 empty] | 0.33333 | 0.5 | 1 | 0.5 |  | 1.1.1 | Q2 1.1 | Provision of Space & Storage | 0.33333 | [7 empty] | 0.33333 |  | 1 | 0.5 |  |  | 1.1.1 | Q2 1.1 | 広さ・収納性 | 0.33333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33333 | 0 | 1 | 0.5 | 0 | 1.1.1 | Q2 1.1 | 広さ・収納性 | 0.33333
1.1.2 | Use of Advanced Information System | 0.33333 | 0 | 0.33333 | 0 |  |  | 1 | 1 | 0.33333 | 0 | 1.1.2 | Q2 1.1 | Use of Advanced Information System | 0.33333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33333 | 0 | 0 | 0.5 | 1 | 1.1.2 | Q2 1.1 | 高度情報通信設備対応 | 0.33333 | [7 empty] | 0.33333 |  |  | 0.5 | 1 | 1.1.2 | Q2 1.1 | 高度情報通信設備対応 | 0.33333 | [7 empty] | 0.33333 |  |  | 0.5 | 1 | 1.1.2 | Q2 1.1 | Use of Advanced Information System | 0.33333 | [7 empty] | 0.33333 |  |  | 0.5 | 1 |  | 1.1.2 | Q2 1.1 | 高度情報通信設備対応 | 0.33333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33333 | 0 | 0 | 0.5 | 1 | 1.1.2 | Q2 1.1 | 高度情報通信設備対応 | 0.33333
1.1.3 | Barrier-free Planning | 0.33333 | 0 | 0.33333 | 0 |  |  | 1 | 0 | 0.33333 | 0 | 1.1.3 | Q2 1.1 | Barrier-free Planning | 0.33333 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.33333 | 1 | 0 | 0 | 0 | 1.1.3 | Q2 1.1 | バリアフリー計画 | 0.33333 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.33333 | 0.5 |  |  |  | 1.1.3 | Q2 1.1 | バリアフリー計画 | 0.33333 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.33333 | 0.5 |  |  |  | 1.1.3 | Q2 1.1 | Barrier-free Planning | 0.33333 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.33333 | 1 |  |  |  |  | 1.1.3 | Q2 1.1 | バリアフリー計画 | 0.33333 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.33333 | 1 | 0 | 0 | 0 | 1.1.3 | Q2 1.1 | バリアフリー計画 | 0.33333
1.2 | Amenity | 0.3 | 0 | 0.3 | 0 | 1 | 0 | 1 | 0 | 0.3 | 0 | 1.2 | Q2 1 | Amenity | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 1.2 | Q2 1 | 心理性・快適性 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 1.2 | Q2 1 | 心理性・快適性 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 1.2 | Q2 1 | Amenity | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 |  | 1.2 | Q2 1 | 心理性・快適性 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 1.2 | Q2 1 | 心理性・快適性 | 0.45
1.2.1 | Perceived Spaciousness & Access to View | 0.33333 | 0 | 0.33333 | 0 |  |  | 1 | 1 | 0.33333 | 0 | 1.2.1 | Q2 1.2 | Perceived Spaciousness & Access to View | 0.33333 | 0.5 | 0.33333 | 0.5 | 0 | 0 | 0 | 0 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.5 | 1.2.1 | Q2 1.2 | 広さ感・景観 | 0.33333 | [12 empty] | 1.2.1 | Q2 1.2 | 広さ感・景観 | 0.33333 | 0.5 | 0.33333 | 0.5 |  |  |  |  | 0.33333 | 0.5 | 0.5 | 0.5 | 0.5 | 1.2.1 | Q2 1.2 | Perceived Spaciousness & Access to View | 0.33333 | 0.5 | 0.33333 | 0.5 |  |  |  |  | 0.33333 | 0.5 | 0.5 | 0.5 | 0.5 |  | 1.2.1 | Q2 1.2 | 広さ感・景観 | 0.33333 | 0.5 | 0.33333 | 0.5 | 0 | 0 | 0 | 0 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.5 | 1.2.1 | Q2 1.2 | 広さ感・景観（天井高） | 0.15
| 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [65 empty] | 1.2.2 | Q2 1.2 | 広さ感・景観（窓） | 0.15
1.2.2 | Space for Refreshment | 0.33333 | 0 | 0.33333 | 0 |  |  | 1 | 0 | 0.33333 | 0 | 1.2.2 | Q2 1.2 | Space for Refreshment | 0.33333 | 0 | 0.33333 | 0 | 0 | 0 | 0 | 0 | 0.33333 | 0 | 0 | 0 | 0 | 1.2.2 | Q2 1.2 | リフレッシュスペース | 0.33333 |  | 0.5 | [10 empty] | 1.2.2 | Q2 1.2 | リフレッシュスペース | 0.33333 | 0 | 0.33333 | [5 empty] | 0.33333 | 0 |  |  |  | 1.2.2 | Q2 1.2 | Space for Refreshment | 0.33333 |  | 0.33333 | [5 empty] | 0.33333 | [5 empty] | 1.2.2 | Q2 1.2 | リフレッシュスペース | 0.33333 | 0 | 0.33333 | 0 | 0 | 0 | 0 | 0 | 0.33333 | 0 | 0 | 0 | 0 | 1.2.3 | Q2 1.2 | リフレッシュスペース | 0.25
1.2.3 | Décor Planning | 0.33333 | 0 | 0.33333 | 0 |  |  | 1 | 1 | 0.33333 | 0 | 1.2.3 | Q2 1.2 | Décor Planning | 0.33333 | 0.5 | 0.33333 | 0.5 | 1 | 1 | 1 | 1 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.5 | 1.2.3 | Q2 1.2 | 内装計画 | 0.33333 | 1 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.2.3 | Q2 1.2 | 内装計画 | 0.33333 | 0.5 | 0.33333 | 0.5 | 1 | 1 | 1 | 1 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.5 | 1.2.3 | Q2 1.2 | Décor Planning | 0.33333 | 0.5 | 0.33333 | 0.5 | 1 | 1 | 1 | 1 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.5 |  | 1.2.3 | Q2 1.2 | 内装計画 | 0.33333 | 0.5 | 0.33333 | 0.5 | 1 | 1 | 1 | 1 | 0.33333 | 0.5 | 0.5 | 0.5 | 0.5 | 1.2.4 | Q2 1.2 | 内装計画 | 0.25
| 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [65 empty] | 1.2.5 | Q2 1.2 | 知的生産性向上の取組み | 0.2
1.3 | Maintenance Management | 0.3 | 0 | 0.3 | 0 | 1 | 0 | 1 | 0 | 0.3 | 0 | 1.3 | Q2 1 | Maintenance Management | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 1.3 | Q2 1 | 維持管理 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 1.3 | Q2 1 | 維持管理 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 1.3 | Q2 1 | Maintenance Management | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | 1.3 | Q2 1 | 維持管理 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 1.3 | Q2 1 | 維持管理 | 0.15
1.3.1 | Design that Considers Maintenance Management | 0.5 | 0 | 0.5 | 0 |  |  | 1 | 0 | 0.5 | 0 | 1.3.1 | Q2 1.3 | Design that Considers Maintenance Management | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 1.3.1 | Q2 1.3 | 総合的な取組み | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 1.3.1 | Q2 1.3 | 維持管理に配慮した設計 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 1.3.1 | Q2 1.3 | Design that Considers Maintenance Management | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | 1.3.1 | Q2 1.3 | 維持管理に配慮した設計 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 1.3.1 | Q2 1.3 | 維持管理に配慮した設計 | 1
1.3.2 | Securing Maintenance Management Functions | 0.5 | 0 | 0.5 | 0 |  |  | 1 | 0 | 0.5 | 0 | 1.3.2 | Q2 1.3 | Securing Maintenance Management Functions | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 1.3.2 | Q2 1.3 | 清掃管理業務 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 1.3.2 | Q2 1.3 | 維持管理用機能の確保 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 1.3.2 | Q2 1.3 | Securing Maintenance Management Functions | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | 1.3.2 | Q2 1.3 | 維持管理用機能の確保 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 1.3.2 | Q2 1.3 | 維持管理用機能の確保 | 0
1.3.3 | Sanitation management operations | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 0 | 1.3.3 | Q2 1.3 | Sanitation management operations | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3.3 | Q2 1.3 | 衛生管理業務 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.3.3 | Q2 1.3 | Sanitation management operations | [14 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
2 | Durability & Reliability | 0.3 | 0 | 0.3 | 0 | 1 | 0 | 1 | 0 | 0.3 | 0 | 2 | Q2 | Durability & Reliability | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 2 | Q2 | 耐用性・信頼性 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 2 | Q2 | 耐用性・信頼性 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 2 | Q2 | Durability & Reliability | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | 2 | Q2 | 耐用性・信頼性 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2 | Q2 | 耐用性・信頼性 | 0.2
2.1 | Earthquake Resistance, Seismic Isolation, Seismic Control, & Vibration Control | 0.5 | 0 | 0.5 | 0 | 1 | 0 | 1 | 0 | 0.5 | 0 | 2.1 | Q2 2 | Earthquake Resistance, Seismic Isolation, Seismic Control, & Vibration Control | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 2.1 | Q2 2 | 耐震･免震 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.1 | Q2 2 | 耐震･免震 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 2.1 | Q2 2 | Earthquake Resistance, Seismic Isolation, Seismic Control, & Vibration Control | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | 2.1 | Q2 2 | 耐震･免震・制震・制振 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 2.1 | Q2 2 | 耐震･免震・制震・制振 | 0.4
2.1.1 | Earthquake-resistance | 0.8 | 0 | 0.8 | 0 |  |  | 1 | 0 | 0.8 | 0 | 2.1.1 | Q2 2.1 | Earthquake-resistance | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0 | 0 | 0 | 2.1.1 | Q2 2.1 | 耐震性 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0 | 0 | 0 | 2.1.1 | Q2 2.1 | 耐震性 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  |  |  | 2.1.1 | Q2 2.1 | Earthquake-resistance | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  |  |  |  | 2.1.1 | Q2 2.1 | 耐震性 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 2.1.1 | Q2 2.1 | 耐震性 | 0.8
2.1.2 | Seismic Isolation, Seismic & Vibration Control | 0.2 | 0 | 0.2 | 0 |  |  | 1 | 0 | 0.2 | 0 | 2.1.2 | Q2 2.1 | Seismic Isolation, Seismic & Vibration Control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.1.2 | Q2 2.1 | 免震・制振性能 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.1.2 | Q2 2.1 | 免震・制振性能 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.1.2 | Q2 2.1 | Seismic Isolation, Seismic & Vibration Control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.1.2 | Q2 2.1 | 免震・制震・制振性能 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1.2 | Q2 2.1 | 免震・制震・制振性能 | 0.2
2.2 | Service Life of Components | 0.3 | 0 | 0.3 | 0 | 1 | 0 | 1 | 0 | 0.3 | 0 | 2.2 | Q2 2 | Service Life of Components | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 2.2 | Q2 2 | 部品・部材の耐用年数 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.2 | Q2 2 | 部品・部材の耐用年数 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 2.2 | Q2 2 | Service Life of Components | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | 2.2 | Q2 2 | 部品・部材の耐用年数 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | Q2 2 | 部品・部材の耐用年数 | 0
2.2.1 | Service Life of Structural Materials | 0.2 | 0 | 0.2 | 0 |  |  | 1 | 0 | 0.2 | 0 | 2.2.1 | Q2 2.2 | Service Life of Structural Materials | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.2.1 | Q2 2.2 | 躯体材料の耐用年数 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0 | 0 | 0 | 2.2.1 | Q2 2.2 | 躯体材料の耐用年数 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.2.1 | Q2 2.2 | Service Life of Structural Materials | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.2.1 | Q2 2.2 | 躯体材料の耐用年数 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2.1 | Q2 2.2 | 躯体材料の耐用年数 | 0
2.2.2 | Necessary Refurbishment Interval for Exterior Finishes | 0.2 | 0 | 0.2 | 0 |  |  | 1 | 0 | 0.2 | 0 | 2.2.2 | Q2 2.2 | Necessary Refurbishment Interval for Exterior Finishes | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.2.2 | Q2 2.2 | 外壁仕上げ材の補修必要間隔 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0 | 0 | 0 | 2.2.2 | Q2 2.2 | 外壁仕上げ材の補修必要間隔 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.2.2 | Q2 2.2 | Necessary Refurbishment Interval for Exterior Finishes | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.2.2 | Q2 2.2 | 外壁仕上げ材の補修必要間隔 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2.2 | Q2 2.2 | 外壁仕上げ材の補修必要間隔 | 0
2.2.3 | Necessary Renewal Interval for Main Interior Finishes | 0.1 | 0 | 0.1 | 0 |  |  | 1 | 0 | 0.1 | 0 | 2.2.3 | Q2 2.2 | Necessary Renewal Interval for Main Interior Finishes | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 2.2.3 | Q2 2.2 | 主要内装仕上げ材の更新必要間隔 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2.3 | Q2 2.2 | 主要内装仕上げ材の更新必要間隔 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 2.2.3 | Q2 2.2 | Necessary Renewal Interval for Main Interior Finishes | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  |  | 2.2.3 | Q2 2.2 | 主要内装仕上げ材の更新必要間隔 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2.3 | Q2 2.2 | 主要内装仕上げ材の更新必要間隔 | 0
2.2.4 | Necessary Renewal Interval for Air Conditioning and Ventilation Ducts | 0.1 | 0 | 0.1 | 0 |  |  | 1 | 0 | 0.1 | 0 | 2.2.4 | Q2 2.2 | Necessary Renewal Interval for Air Conditioning and Ventilation Ducts | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 2.2.4 | Q2 2.2 | 空調換気ダクトの更新必要間隔 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 2.2.4 | Q2 2.2 | 空調換気ダクトの更新必要間隔 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 2.2.4 | Q2 2.2 | Necessary Renewal Interval for Air Conditioning and Ventilation Ducts | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  |  | 2.2.4 | Q2 2.2 | 空調換気ダクトの更新必要間隔 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2.4 | Q2 2.2 | 空調換気ダクトの更新必要間隔 | 0
2.2.5 | Necessary Renewal Interval for HVAC and Water Supply and Drainage Pipes | 0.2 | 0 | 0.2 | 0 |  |  | 1 | 0 | 0.2 | 0 | 2.2.5 | Q2 2.2 | Necessary Renewal Interval for HVAC and Water Supply and Drainage Pipes | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.2.5 | Q2 2.2 | 空調・給排水配管の更新必要間隔 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 2.2.5 | Q2 2.2 | 空調・給排水配管の更新必要間隔 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.2.5 | Q2 2.2 | Necessary Renewal Interval for HVAC and Water Supply and Drainage Pipes | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.2.5 | Q2 2.2 | 空調・給排水配管の更新必要間隔 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2.5 | Q2 2.2 | 空調・給排水配管の更新必要間隔 | 0
2.2.6 | Necessary Replacement Interval for Major Equipment and Services | 0.2 | 0 | 0.2 | 0 |  |  | 1 | 0 | 0.2 | 0 | 2.2.6 | Q2 2.2 | Necessary Replacement Interval for Major Equipment and Services | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.2.6 | Q2 2.2 | 主要設備機器の更新必要間隔 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0 | 0 | 0 | 2.2.6 | Q2 2.2 | 主要設備機器の更新必要間隔 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.2.6 | Q2 2.2 | Necessary Replacement Interval for Major Equipment and Services | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.2.6 | Q2 2.2 | 主要設備機器の更新必要間隔 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2.6 | Q2 2.2 | 主要設備機器の更新必要間隔 | 0
2.3 | Appropriate Renewal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | Q2 2 | Appropriate Renewal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | Q2 2 | 適切な更新 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3 | Q2 2 | 適切な更新 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2.3 | Q2 2 | Appropriate Renewal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2.3 | Q2 2 | 適切な更新 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | Q2 2 | 適切な更新 | 0
2.3.1 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 0 | 2.3.1 | Q2 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3.1 | Q2 2.3 | 屋上（屋根）・外壁仕上げ材の更新 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 2.3.1 | Q2 2.3 | 屋上（屋根）・外壁仕上げ材の更新 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2.3.1 | Q2 2.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2.3.1 | Q2 2.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3.1 | Q2 2.3 | 屋上（屋根）・外壁仕上げ材の更新 | 0
2.3.2 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 0 | 2.3.2 | Q2 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3.2 | Q2 2.3 | 配管・配線材の更新 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 2.3.2 | Q2 2.3 | 配管・配線材の更新 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2.3.2 | Q2 2.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2.3.2 | Q2 2.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3.2 | Q2 2.3 | 配管・配線材の更新 | 0
2.3.3 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 0 | 2.3.3 | Q2 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3.3 | Q2 2.3 | 主要設備機器の更新 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 2.3.3 | Q2 2.3 | 主要設備機器の更新 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2.3.3 | Q2 2.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2.3.3 | Q2 2.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3.3 | Q2 2.3 | 主要設備機器の更新 | 0
2.4 | Reliability | 0.2 | 0 | 0.2 | 0 | 1 | 0 | 1 | 0 | 0.2 | 0 | 2.4 | Q2 2 | Reliability | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4 | Q2 2 | 信頼性 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.4 | Q2 2 | 信頼性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.4 | Q2 2 | Reliability | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.4 | Q2 2 | 信頼性 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 2.4 | Q2 2 | 信頼性 | 0.6
2.4.1 | HVAC System | 0.2 | 0 | 0.2 | 0 |  |  | 1 | 0 | 0.2 | 0 | 2.4.1 | Q2 2.4 | HVAC System | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.1 | Q2 2.4 | 空調・換気設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.1 | Q2 2.4 | 空調・換気設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.4.1 | Q2 2.4 | HVAC System | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.4.1 | Q2 2.4 | 空調・換気設備 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4.1 | Q2 2.4 | 空調・換気設備 | 0.15
2.4.2 | Water Supply & Drainage | 0.2 | 0 | 0.2 | 0 |  |  | 1 | 0 | 0.2 | 0 | 2.4.2 | Q2 2.4 | Water Supply & Drainage | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.2 | Q2 2.4 | 給排水・衛生設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.2 | Q2 2.4 | 給排水・衛生設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.4.2 | Q2 2.4 | Water Supply & Drainage | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.4.2 | Q2 2.4 | 給排水・衛生設備 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4.2 | Q2 2.4 | 給排水・衛生設備 | 0.15
2.4.3 | Electrical Equipment | 0.2 | 0 | 0.2 | 0 |  |  | 1 | 0 | 0.2 | 0 | 2.4.3 | Q2 2.4 | Electrical Equipment | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.3 | Q2 2.4 | 電気設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.3 | Q2 2.4 | 電気設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.4.3 | Q2 2.4 | Electrical Equipment | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.4.3 | Q2 2.4 | 電気設備 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4.3 | Q2 2.4 | 電気設備 | 0.25
2.4.4 | Support Method of Machines & Ducts | 0.2 | 0 | 0.2 | 0 |  |  | 1 | 0 | 0.2 | 0 | 2.4.4 | Q2 2.4 | Support Method of Machines & Ducts | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.4 | Q2 2.4 | 機械・配管支持方法 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.4 | Q2 2.4 | 機械・配管支持方法 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.4.4 | Q2 2.4 | Support Method of Machines & Ducts | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.4.4 | Q2 2.4 | 機械・配管支持方法 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 2.4.4 | Q2 2.4 | 機械・配管支持方法 | 0.2
2.4.5 | Communications & IT Equipment | 0.2 | 0 | 0.2 | 0 |  |  | 1 | 0 | 0.2 | 0 | 2.4.5 | Q2 2.4 | Communications & IT Equipment | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.5 | Q2 2.4 | 通信・情報設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4.5 | Q2 2.4 | 通信・情報設備 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.4.5 | Q2 2.4 | Communications & IT Equipment | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.4.5 | Q2 2.4 | 通信・情報設備 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4.5 | Q2 2.4 | 通信・情報設備 | 0.25
0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  | 0 | Q | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Q |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Q | [15 empty] | Q | [16 empty] | Q |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Q |  | 0
3 | Flexibility & Adaptability | 0.3 | 0 | 0.3 | 0 | 1 | 0 | 1 | 0 | 0.3 | 0 | 3 | Q2 | Flexibility & Adaptability | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 3 | Q2 | 対応性・更新性 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 3 | Q2 | 対応性・更新性 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 3 | Q2 | Flexibility & Adaptability | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | 3 | Q2 | 対応性・更新性 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | Q2 | 対応性・更新性 | 0.2
3.1 | Spatial Margin | 0.3 | 0 | 0.3 | 0 | 1 | 0 | 1 | 0 | 0.3 | 0 | 3.1 | Q2 3 | Spatial Margin | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 3.1 | Q2 3 | 空間のゆとり | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 3.1 | Q2 3 | 空間のゆとり | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 3.1 | Q2 3 | Spatial Margin | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 |  | 3.1 | Q2 3 | 空間のゆとり | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | Q2 3 | 空間のゆとり | 0.3
3.1.1 | Allowance for Floor-to-floor Height | 0.6 | 0 | 0.6 | 0 |  |  | 1 | 1 | 0.6 | 0 | 3.1.1 | Q2 3.1 | Allowance for Floor-to-floor Height | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0 | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 3.1.1 | Q2 3.1 | 階高のゆとり | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  |  | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 3.1.1 | Q2 3.1 | 階高のゆとり | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  |  | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 3.1.1 | Q2 3.1 | Allowance for Floor-to-floor Height | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  |  | 0 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  | 3.1.1 | Q2 3.1 | 階高のゆとり | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1.1 | Q2 3.1 | 階高のゆとり | 0
3.1.2 | Flexibility in Floor Layout | 0.4 | 0 | 0.4 | 0 |  |  | 1 | 1 | 0.4 | 0 | 3.1.2 | Q2 3.1 | Flexibility in Floor Layout | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 3.1.2 | Q2 3.1 | 空間の形状・自由さ | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  | 1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 3.1.2 | Q2 3.1 | 空間の形状・自由さ | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  | 1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 3.1.2 | Q2 3.1 | Flexibility in Floor Layout | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  | 1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  | 3.1.2 | Q2 3.1 | 空間の形状・自由さ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1.2 | Q2 3.1 | 空間の形状・自由さ | 1
3.2 | Floor Load Margin | 0.3 | 0 | 0.3 | 0 |  |  | 1 | 1 | 0.3 | 0 | 3.2 | Q2 3 | Floor Load Margin | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 3.2 | Q2 3 | 荷重のゆとり | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 3.2 | Q2 3 | 荷重のゆとり | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 3.2 | Q2 3 | Floor Load Margin | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 |  | 3.2 | Q2 3 | 荷重のゆとり | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | Q2 3 | 荷重のゆとり | 0.3
3.3 | System Renewability | 0.4 | 0 | 0.4 | 0 | 1 | 0 | 1 | 0 | 0.4 | 0 | 3.3 | Q2 3 | System Renewability | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1 | 1 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 3.3 | Q2 3 | 設備の更新性 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1 | 1 | 0.4 | 0.4 | 0.4 |  |  |  | 3.3 | Q2 3 | 設備の更新性 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1 | 1 | 0.4 | 0.4 | 0.4 |  |  |  | 3.3 | Q2 3 | System Renewability | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 1 | 1 | 0.4 | 0.4 | 0.4 |  |  |  |  | 3.3 | Q2 3 | 設備の更新性 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | Q2 3 | 設備の更新性 | 0.4
3.3.1 | Ease of Air Conditioning Duct Renewal | 0.2 | 0 | 0.2 | 0 |  |  | 1 | 0 | 0.2 | 0 | 3.3.1 | Q2 3.3 | Ease of Air Conditioning Duct Renewal | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 3.3.1 | Q2 3.3 | 空調配管の更新性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3.1 | Q2 3.3 | 空調配管の更新性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3.1 | Q2 3.3 | Ease of Air Conditioning Duct Renewal | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 3.3.1 | Q2 3.3 | 空調配管の更新性 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3.1 | Q2 3.3 | 空調配管の更新性 | 0
3.3.2 | Ease of Water Supply and Drain Pipe Renewal | 0.2 | 0 | 0.2 | 0 |  |  | 1 | 0 | 0.2 | 0 | 3.3.2 | Q2 3.3 | Ease of Water Supply and Drain Pipe Renewal | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 3.3.2 | Q2 3.3 | 給排水管の更新性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3.2 | Q2 3.3 | 給排水管の更新性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3.2 | Q2 3.3 | Ease of Water Supply and Drain Pipe Renewal | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 3.3.2 | Q2 3.3 | 給排水管の更新性 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3.2 | Q2 3.3 | 給排水管の更新性 | 0.4
3.3.3 | Ease of Electrical Wiring Renewal | 0.1 | 0 | 0.1 | 0 |  |  | 1 | 0 | 0.1 | 0 | 3.3.3 | Q2 3.3 | Ease of Electrical Wiring Renewal | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 3.3.3 | Q2 3.3 | 電気配線の更新性 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 3.3.3 | Q2 3.3 | 電気配線の更新性 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 3.3.3 | Q2 3.3 | Ease of Electrical Wiring Renewal | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  |  | 3.3.3 | Q2 3.3 | 電気配線の更新性 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3.3 | Q2 3.3 | 電気配線の更新性 | 0.1
3.3.4 | Ease of Communications Cable Renewal | 0.1 | 0 | 0.1 | 0 |  |  | 1 | 0 | 0.1 | 0 | 3.3.4 | Q2 3.3 | Ease of Communications Cable Renewal | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 3.3.4 | Q2 3.3 | 通信配線の更新性 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 3.3.4 | Q2 3.3 | 通信配線の更新性 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 3.3.4 | Q2 3.3 | Ease of Communications Cable Renewal | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  |  | 3.3.4 | Q2 3.3 | 通信配線の更新性 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3.4 | Q2 3.3 | 通信配線の更新性 | 0.1
3.3.5 | Ease of Equipment Renewal | 0.2 | 0 | 0.2 | 0 |  |  | 1 | 0 | 0.2 | 0 | 3.3.5 | Q2 3.3 | Ease of Equipment Renewal | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 3.3.5 | Q2 3.3 | 設備機器の更新性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3.5 | Q2 3.3 | 設備機器の更新性 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3.5 | Q2 3.3 | Ease of Equipment Renewal | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 3.3.5 | Q2 3.3 | 設備機器の更新性 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3.5 | Q2 3.3 | 設備機器の更新性 | 0.2
3.3.6 | Provision of Backup Space | 0.2 | 0 | 0.2 | 0 |  |  | 1 | 0 | 0.2 | 0 | 3.3.6 | Q2 3.3 | Provision of Backup Space | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 3.3.6 | Q2 3.3 | バックアップスペースの確保 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3.6 | Q2 3.3 | バックアップスペースの確保 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3.6 | Q2 3.3 | Provision of Backup Space | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 3.3.6 | Q2 3.3 | バックアップスペースの確保 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3.6 | Q2 3.3 | バックアップスペースの確保 | 0.2
Q3 | Outdoor Environment on Site | 0.3 | 0 | 0.3 | 0 | 1 | 0 | 1 |  | 0.3 | 0 | Q3 | Q | Outdoor Environment on Site | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0 | 0 | 0 | Q3 | Q | 室外環境（敷地内） | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0 | 0 | 0 | Q3 | Q | 室外環境（敷地内） | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 |  |  |  | Q3 | Q | Outdoor Environment on Site | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 |  |  |  |  | Q3 | Q | 室外環境（敷地内） | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.5 | 0.35 | 0 | 0 | 0 | Q3 | Q | 室外環境（敷地内） | 0.1
1 | Preservation & Creation of Biotope | 0.3 | 0 | 0.3 | 0 |  |  | 1 | 0 | 0.3 | 0 | 1 | Q3 | Preservation & Creation of Biotope | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 1 | Q3 | 生物資源の保全と創出 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 1 | Q3 | 生物資源の保全と創出 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 1 | Q3 | Preservation & Creation of Biotope | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | 1 | Q3 | 生物資源の保全と創出 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 1 | Q3 | 生物資源の保全と創出 | 0
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [65 empty] | 1 | Q3 | 豊かな室外環境 | 1
1.1 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [65 empty] | 3.1 | Q3 3 | 知的生産性向上の取組み | 1
2 | Townscape & Landscape | 0.4 | 0 | 0.4 | 0 |  |  | 1 | 0 | 0.4 | 0 | 2 | Q3 | Townscape & Landscape | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 2 | Q3 | まちなみ・景観への配慮 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 2 | Q3 | まちなみ・景観への配慮 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | 2 | Q3 | Townscape & Landscape | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  |  | 2 | Q3 | まちなみ・景観への配慮 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 2 | Q3 | まちなみ・景観への配慮 | 0
3 | Local Characteristics & Outdoor Amenity | 0.3 | 0 | 0.3 | 0 | 1 | 0 | 1 | 0 | 0.3 | 0 | 3 | Q3 | Local Characteristics & Outdoor Amenity | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 3 | Q3 | 地域性・アメニティへの配慮 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 3 | Q3 | 地域性・アメニティへの配慮 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 3 | Q3 | Local Characteristics & Outdoor Amenity | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | 3 | Q3 | 地域性・アメニティへの配慮 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 3 | Q3 | 地域性・アメニティへの配慮 | 0
3.1 | Attention to Local Character & Improvement of Comfort | 0.5 | 0 | 0.5 | 0 |  |  | 1 | 0 | 0.5 | 0 | 3.1 | Q3 3 | Attention to Local Character & Improvement of Comfort | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 3.1 | Q3 3 | 地域性への配慮、快適性の向上 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 3.1 | Q3 3 | 地域性への配慮、快適性の向上 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 3.1 | Q3 3 | Attention to Local Character & Improvement of Comfort | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | 3.1 | Q3 3 | 地域性への配慮、快適性の向上 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 3.1 | Q3 3 | 地域性への配慮、快適性の向上 | 0
3.2 | Improvement of the Thermal Environment on Site | 0.5 | 0 | 0.5 | 0 |  |  | 1 | 0 | 0.5 | 0 | 3.2 | Q3 3 | Improvement of the Thermal Environment on Site | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 3.2 | Q3 3 | 敷地内温熱環境の向上 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 3.2 | Q3 3 | 敷地内温熱環境の向上 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 3.2 | Q3 3 | Improvement of the Thermal Environment on Site | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | 3.2 | Q3 3 | 敷地内温熱環境の向上 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 3.2 | Q3 3 | 敷地内温熱環境の向上 | 0
0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  | 0 | Q | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Q |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Q | [15 empty] | Q | [16 empty] | Q |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Q |  | 0
LR | Environmental Load Reduction of Building |  |  | #VALUE! | 0 | #VALUE! | 0 | #VALUE! | 0 | 0 | 0 | LR |  | Environmental Load Reduction of Building | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LR |  | 建築物の環境負荷低減性 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LR |  | 建築物の環境負荷低減性 | [13 empty] | LR |  | Environmental Load Reduction of Building | [14 empty] | LR |  | 建築物の環境負荷低減性 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LR |  | 建築物の環境負荷低減性 | 0
LR1 | Energy | #VALUE! | 0 | 0.4 | 0 | 1 | 0 | 1 |  | 0.4 | 0 | LR1 | LR | Energy | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | LR1 | LR | エネルギー | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | LR1 | LR | エネルギー | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | LR1 | LR | Energy | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  |  | LR1 | LR | エネルギー | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | LR1 | LR | エネルギー | 0.55
1 | Control of Heat Load on Building Envelopes | 0.2 | 0 | 0.2 | 0 |  |  | 1 | 0 | 0.2 | 0 | 1 | LR1 | Control of Heat Load on Building Envelopes | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 1 | LR1 | 建物外皮の熱負荷抑制 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 0.2 |  |  |  | 1 | LR1 | 建物外皮の熱負荷抑制 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 1 | LR1 | Control of Heat Load on Building Envelopes | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 1 | LR1 | 建物外皮の熱負荷抑制 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 1 | LR1 | 建物外皮の熱負荷抑制 | 0.2
2 | Natural Energy Utilization (Direct Use) | 0.1 | 0 | 0.1 | 0 | 0 | 0 | 1 | 0 | 0.1 | 0 | 2 | LR1 | Natural Energy Utilization (Direct Use) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 2 | LR1 | 自然エネルギー利用 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.125 | 0.1 |  |  |  | 2 | LR1 | 自然エネルギー利用 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 2 | LR1 | Natural Energy Utilization (Direct Use) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  |  | 2 | LR1 | 自然エネルギー利用 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 2 | LR1 | 自然エネルギー利用 | 0.1
0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | LR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | LR | 実施・竣工 | [14 empty] | LR | 定量評価 | [14 empty] | LR | [16 empty] | LR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | LR |  | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | LR | 基本 | [14 empty] | LR | 定性評価 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | LR | [16 empty] | LR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | LR |  | 0
2.1 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 2.1 | LR1 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | LR1 2 | 自然エネルギーの直接利用 | [13 empty] | 2.1 | LR1 2 | 自然エネルギーの直接利用 | [13 empty] | 2.1 | LR1 2 | [15 empty] | 2.1 | LR1 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | LR1 2 |  | 0
2.2 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 2.2 | LR1 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | LR1 2 | 自然エネルギーの変換利用 | [13 empty] | 2.2 | LR1 2 | 自然エネルギーの変換利用 | [13 empty] | 2.2 | LR1 2 | [15 empty] | 2.2 | LR1 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | LR1 2 |  | 0
3 | Efficiency in Building Service System | 0.5 | 0 | 0.5 | 0 | 0 | 0 | 1 | 0 | 0.5 | 0 | 3 | LR1 | Efficiency in Building Service System | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 3 | LR1 | 設備システムの高効率化 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.625 | 0.5 |  |  |  | 3 | LR1 | 設備システムの高効率化 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 3 | LR1 | Efficiency in Building Service System | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | 3 | LR1 | 設備システムの高効率化 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 3 | LR1 | 設備システムの高効率化 | 0.5
3.1 | Other than apartment | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 1 | 0 | 3.1 | LR1 3 | Other than apartment | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 3a | LR1 3 | ERRによる評価 | [13 empty] | 3a | LR1 3 | 非住宅部分 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  |  | 3.1 | LR1 3 | Other than apartment | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  |  |  | 3a.3b | LR1 3 | 非住宅部分 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 3a.3b | LR1 3 | 非住宅部分 | 1
3.2 | Apartment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | LR1 3 | Apartment | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3b | LR1 3 | ERR以外による評価 | [13 empty] | 3b | LR1 3 | 集合住宅 | [6 empty] | 1 | [6 empty] | 3.2 | LR1 3 | Apartment | [6 empty] | 1 | [7 empty] | 3b.c | LR1 3 | 集合住宅の評価 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3b.c | LR1 3 | 集合住宅の評価 | 0
3.1 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 3.1 | LR1 3b | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | LR1 3b | 空調設備 | [9 empty] | 0.65 |  |  |  | 3.1 | LR1 3b | 空調設備 | [9 empty] | 0.65 |  |  |  | 3.1 | LR1 3b | [14 empty] | 127 | 3.1 | LR1 3b |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | LR1 3b |  | 0
3.2 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 3.2 | LR1 3b | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | LR1 3b | 換気設備 | [9 empty] | 0.1 |  |  |  | 3.2 | LR1 3b | 換気設備 | [9 empty] | 0.1 |  |  |  | 3.2 | LR1 3b | [14 empty] | 128 | 3.2 | LR1 3b |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | LR1 3b |  | 0
3.3 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 3.3 | LR1 3b | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | LR1 3b | 照明設備 | [9 empty] | 0.2 |  |  |  | 3.3 | LR1 3b | 照明設備 | [9 empty] | 0.2 |  |  |  | 3.3 | LR1 3b | [14 empty] | 129 | 3.3 | LR1 3b |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | LR1 3b |  | 0
3.4 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 3.4 | LR1 3b | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | LR1 3b | 給湯設備 | [9 empty] | 0.05 |  |  |  | 3.4 | LR1 3b | 給湯設備 | [9 empty] | 0.05 |  |  |  | 3.4 | LR1 3b | [14 empty] | 130 | 3.4 | LR1 3b |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | LR1 3b |  | 0
3.5 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 3.5 | LR1 3b | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | LR1 3b | 昇降機設備 | [13 empty] | 3.5 | LR1 3b | 昇降機設備 | [13 empty] | 3.5 | LR1 3b | [14 empty] | 131 | 3.5 | LR1 3b |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | LR1 3b |  | 0
0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | LR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | LR | [15 empty] | LR | [15 empty] | LR | [14 empty] | 132 |  | LR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | LR |  | 0
4 | Initiatives for Efficient Operation | 0.2 | 0 | 0.2 | 0 | 1 | 0 | 1 | 0 | 0.2 | 0 | 4 | LR1 | Initiatives for Efficient Operation | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 4 | LR1 | 効率的運用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.2 |  |  |  | 4 | LR1 | 効率的運用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 4 | LR1 | Initiatives for Efficient Operation | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 133 | 4 | LR1 | 効率的運用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 4 | LR1 | 効率的運用 | 0.2
4.1 | Other than apartments | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 4.1 | LR1 4 | Other than apartments | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 4.1 | LR1 4 | 住宅以外の評価 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  |  | 4.1 | LR1 4 | 住宅以外の評価 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  |  | 4.1 | LR1 4 | Other than apartments | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 |  |  |  | 134 | 4.1 | LR1 4 | 住宅以外の評価 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 4.1 | LR1 4 | 住宅以外の評価 | 1
4.1.1 | Monitoring | 0.4 | 0 | 0.4 | 0 |  |  | 1 | 0 | 0.4 | 0 | 4.1.1 | LR1 4.1 | Monitoring | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 4.1.1 | LR1 4.1 | モニタリング | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 0.5 | 0.5 | 0.5 |  |  |  | 4.1.1 | LR1 4.1 | モニタリング | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 0.5 | 0.5 | 0.5 |  |  |  | 4.1.1 | LR1 4.1 | Monitoring | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  | 0.4 | 0.4 | 0.4 |  |  |  |  | 4.1.1 | LR1 4.1 | モニタリング | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 4.1.1 | LR1 4.1 | モニタリング | 0.4
4.1.2 | Operation & Management System | 0.4 | 0 | 0.4 | 0 |  |  | 1 | 0 | 0.4 | 0 | 4.1.2 | LR1 4.1 | Operation & Management System | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 4.1.2 | LR1 4.1 | 運用管理体制 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 0.5 | 0.5 | 0.5 |  |  |  | 4.1.2 | LR1 4.1 | 運用管理体制 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 0.5 | 0.5 | 0.5 |  |  |  | 4.1.2 | LR1 4.1 | Operation & Management System | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  | 0.4 | 0.4 | 0.4 |  |  |  |  | 4.1.2 | LR1 4.1 | 運用管理体制 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 4.1.2 | LR1 4.1 | 運用管理体制 | 0.4
4.1.3 | Expanding adoption of non-fossil energy | 0.1 | 0 | 0.1 | 0 |  |  | 1 | 0 | 0.1 | 0 | 4.1.3 | LR1 4.1 | Expanding adoption of non-fossil energy | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | [32 empty] | 4.1.3 | LR1 4.1 | Expanding adoption of non-fossil energy | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.1 | 0.1 | 0.1 | [7 empty] | 0.1 | [15 empty] | 0.1
4.1.4 | Promoting Commissioning | 0.1 | 0 | 0.1 | 0 |  |  | 1 | 0 | 0.1 | 0 | 4.1.4 | LR1 4.1 | Promoting Commissioning | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | [32 empty] | 4.1.4 | LR1 4.1 | Promoting Commissioning | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  | 0.1 | 0.1 | 0.1 | [7 empty] | 0.1 | [15 empty] | 0.1
4.2 | Apartments | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | LR1 4 | Apartments | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | LR1 4 | 住宅の評価 | [6 empty] | 1 | [6 empty] | 4.2 | LR1 4 | 住宅の評価 | [6 empty] | 1 | [6 empty] | 4.2 | LR1 4 | Apartments | [6 empty] | 1 | [7 empty] | 4.2 | LR1 4 | 住宅の評価 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | LR1 4 | 住宅の評価 | 0
4.2.1 | Monitoring | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 0 | 4.2.1 | LR1 4.2 | Monitoring | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2.1 | LR1 4.2 | 住まい方の提示 | [6 empty] | 0.5 | [6 empty] | 4.2.1 | LR1 4.2 | モニタリング | [6 empty] | 0.5 | [6 empty] | 4.2.1 | LR1 4.2 | Monitoring | [6 empty] | 0.5 | [7 empty] | 4.2.1 | LR1 4.2 | モニタリング | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2.1 | LR1 4.2 | モニタリング | 0
4.2.2 | Operation & Management System | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 0 | 4.2.2 | LR1 4.2 | Operation & Management System | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2.2 | LR1 4.2 | エネルギーの管理と制御 | [6 empty] | 0.5 | [6 empty] | 4.2.2 | LR1 4.2 | 運用管理体制 | [6 empty] | 0.5 | [6 empty] | 4.2.2 | LR1 4.2 | Operation & Management System | [6 empty] | 0.5 | [7 empty] | 4.2.2 | LR1 4.2 | 運用管理体制 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2.2 | LR1 4.2 | 運用管理体制 | 0
LR2 | Resources & Materials | #VALUE! | 0 | 0.3 | 0 | 1 | 0 | 1 |  | 0.3 | 0 | LR2 | LR | Resources & Materials | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | LR2 | LR | 資源・マテリアル | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | LR2 | LR | 資源・マテリアル | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | LR2 | LR | Resources & Materials | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | LR2 | LR | 資源・マテリアル | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | LR2 | LR | 資源・マテリアル | 0.35
1 | Water Resources | 0.2 | 0 | 0.2 | 0 | 1 | 0 | 1 | 0 | 0.2 | 0 | 1 | LR2 | Water Resources | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 1 | LR2 | 水資源保護 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 1 | LR2 | 水資源保護 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 1 | LR2 | Water Resources | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 1 | LR2 | 水資源保護 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 1 | LR2 | 水資源保護 | 0.3
1.1 | Water Saving | 0.4 | 0 | 0.4 | 0 |  |  | 1 | 0 | 0.4 | 0 | 1.1 | LR2 1 | Water Saving | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 1.1 | LR2 1 | 節水 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | 1.1 | LR2 1 | 節水 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | 1.1 | LR2 1 | Water Saving | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  |  | 1.1 | LR2 1 | 節水 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 1.1 | LR2 1 | 節水 | 0.4
1.2 | Rain Water & Waste Water Use | 0.6 | 0 | 0.6 | 0 | 1 | 0 | 1 | 0 | 0.6 | 0 | 1.2 | LR2 1 | Rain Water & Waste Water Use | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0 | 0 | 1.2 | LR2 1 | 雨水利用・雑排水再利用 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  |  |  | 1.2 | LR2 1 | 雨水利用・雑排水再利用 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  |  |  | 1.2 | LR2 1 | Rain Water & Waste Water Use | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  |  |  |  | 1.2 | LR2 1 | 雨水利用・雑排水再利用 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0 | 0 | 1.2 | LR2 1 | 雨水利用・雑排水再利用 | 0.6
1.2.1 | Rainwater Use System | 0.7 | 0 | 0.7 | 0 |  |  | 1 | 0 | 0.7 | 0 | 1.2.1 | LR2 1.2 | Rainwater Use System | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 1.2.1 | LR2 1.2 | 雨水利用システム導入の有無 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 |  |  |  | 1.2.1 | LR2 1.2 | 雨水利用システム導入の有無 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 |  |  |  | 1.2.1 | LR2 1.2 | Rainwater Use System | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 |  |  |  |  | 1.2.1 | LR2 1.2 | 雨水利用システム導入の有無 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 1.2.1 | LR2 1.2 | 雨水利用システム導入の有無 | 0.7
1.2.2 | Waste Water Reuse System | 0.3 | 0 | 0.3 | 0 |  |  | 1 | 0 | 0.3 | 0 | 1.2.2 | LR2 1.2 | Waste Water Reuse System | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 1.2.2 | LR2 1.2 | 雑排水等再利用システム導入の有無 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 1.2.2 | LR2 1.2 | 雑排水等再利用システム導入の有無 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 1.2.2 | LR2 1.2 | Waste Water Reuse System | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | 1.2.2 | LR2 1.2 | 雑排水等再利用システム導入の有無 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 1.2.2 | LR2 1.2 | 雑排水等再利用システム導入の有無 | 0.3
2 | Reducing Use of Non-renewable Resources | 0.6 | 0 | 0.6 | 0 | 1 | 0 | 1 | 0 | 0.6 | 0 | 2 | LR2 | Reducing Use of Non-renewable Resources | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0 | 0 | 0 | 2 | LR2 | 非再生性資源の使用量削減 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  |  |  | 2 | LR2 | 非再生性資源の使用量削減 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  |  |  | 2 | LR2 | Reducing Use of Non-renewable Resources | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  |  |  |  | 2 | LR2 | 非再生性資源の使用量削減 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 2 | LR2 | 非再生性資源の使用量削減 | 0.5
2.1 | Reducing Use of Materials | 0.1 | 0 | 0.1 | 0 |  |  | 1 | 0 | 0.1 | 0 | 2.1 | LR2 2 | Reducing Use of Materials | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 2.1 | LR2 2 | 材料使用量の削減 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 2.1 | LR2 2 | 材料使用量の削減 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 2.1 | LR2 2 | Reducing Use of Materials | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  |  | 2.1 | LR2 2 | 材料使用量の削減 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | LR2 2 | 材料使用量の削減 | 0
2.2 | Continuing Use of Existing Structural Frame, etc. | 0.2 | 0 | 0.2 | 0 |  |  | 1 | 0 | 0.2 | 0 | 2.2 | LR2 2 | Continuing Use of Existing Structural Frame, etc. | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.2 | LR2 2 | 既存建築躯体等の継続使用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.2 | LR2 2 | 既存建築躯体等の継続使用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.2 | LR2 2 | Continuing Use of Existing Structural Frame, etc. | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.2 | LR2 2 | 既存建築躯体等の継続使用 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | LR2 2 | 既存建築躯体等の継続使用 | 0
2.3 | Use of Recycled Materials as Structural Materials | 0.2 | 0 | 0.2 | 0 |  |  | 1 | 0 | 0.2 | 0 | 2.3 | LR2 2 | Use of Recycled Materials as Structural Materials | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.3 | LR2 2 | 躯体材料におけるリサイクル材の使用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.3 | LR2 2 | 躯体材料におけるリサイクル材の使用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.3 | LR2 2 | Use of Recycled Materials as Structural Materials | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.3 | LR2 2 | 躯体材料におけるリサイクル材の使用 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0 | 0 | 2.3 | LR2 2 | 躯体材料におけるリサイクル材の使用 | 0
2.4 | Use of Recycled Materials as Non-structural Materials | 0.2 | 0 | 0.2 | 0 |  |  | 1 | 0 | 0.2 | 0 | 2.4 | LR2 2 | Use of Recycled Materials as Non-structural Materials | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.4 | LR2 2 | 躯体材料以外におけるリサイクル材の使用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.4 | LR2 2 | 躯体材料以外におけるリサイクル材の使用 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.4 | LR2 2 | Use of Recycled Materials as Non-structural Materials | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.4 | LR2 2 | 躯体材料以外におけるリサイクル材の使用 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0 | 2.4 | LR2 2 | 躯体材料以外におけるリサイクル材の使用 | 0.2
2.5 | Timber from Sustainable Forestry | 0.1 | 0 | 0.1 | 0 |  |  | 1 | 0 | 0.1 | 0 | 2.5 | LR2 2 | Timber from Sustainable Forestry | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 2.5 | LR2 2 | 持続可能な森林から産出された木材 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 2.5 | LR2 2 | 持続可能な森林から産出された木材 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  | 2.5 | LR2 2 | Timber from Sustainable Forestry | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  |  |  | 2.5 | LR2 2 | 持続可能な森林から産出された木材 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0 | 2.5 | LR2 2 | 持続可能な森林から産出された木材 | 0.4
2.6 | Reusability of Components and Materials | 0.2 | 0 | 0.2 | 0 |  |  | 1 | 0 | 0.2 | 0 | 2.6 | LR2 2 | Reusability of Components and Materials | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.6 | LR2 2 | 部材の再利用可能性向上への取組み | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.6 | LR2 2 | 部材の再利用可能性向上への取組み | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 2.6 | LR2 2 | Reusability of Components and Materials | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 2.6 | LR2 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | LR2 2 | 部材の再利用可能性向上への取組み | 0.4
2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | LR2 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 2.6 | LR2 2 | [15 empty] | 2.6 | LR2 2 | 部材の再利用可能性向上への取組み（TC) | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0 | 0 | 0 | 2.6 | LR2 2 |  | 0
2.6.1 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 0 | 2.6.1 | LR2 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 2.6.1 | LR2 2.2 | [15 empty] | 2.6.1 | LR2 2.2 | 躯体のリサイクル・リユース | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.6.1 | LR2 2.2 |  | 0
2.6.2 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 0 | 2.6.2 | LR2 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 2.6.2 | LR2 2.2 | [15 empty] | 2.6.2 | LR2 2.2 | 屋根材のリサイクル・リユース | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 2.6.2 | LR2 2.2 |  | 0
2.6.3 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 0 | 2.6.3 | LR2 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 2.6.3 | LR2 2.2 | [15 empty] | 2.6.3 | LR2 2.2 | 外壁材のリサイクル・リユース | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 2.6.3 | LR2 2.2 |  | 0
2.6.4 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 0 | 2.6.4 | LR2 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 2.6.4 | LR2 2.2 | [15 empty] | 2.6.4 | LR2 2.2 | 内装材のリサイクル・リユース | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 2.6.4 | LR2 2.2 |  | 0
2.6.5 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 0 | 2.6.5 | LR2 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 2.6.5 | LR2 2.2 | [15 empty] | 2.6.5 | LR2 2.2 | 設備機器のリサイクル・リユース | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 2.6.5 | LR2 2.2 |  | 0
2.6.6 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 0 | 2.6.6 | LR2 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 2.6.6 | LR2 2.2 | [15 empty] | 2.6.6 | LR2 2.2 | 外構資材のリユース | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 2.6.6 | LR2 2.2 |  | 0
2.7 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 0 | 2.7 | LR2 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [32 empty] | 2.7 | LR2 2 | [15 empty] | 2.7 | LR2 2 | 廃棄物発生量の最小化 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 2.7 | LR2 2 |  | 0
3 | Avoiding the Use of Materials with Pollutant Content | 0.2 | 0 | 0.2 | 0 | 1 | 0 | 1 | 0 | 0.2 | 0 | 3 | LR2 | Avoiding the Use of Materials with Pollutant Content | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 3 | LR2 | 汚染物質含有材料の使用回避 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 3 | LR2 | 汚染物質含有材料の使用回避 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3 | LR2 | Avoiding the Use of Materials with Pollutant Content | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 3 | LR2 | 汚染物質含有材料の使用回避 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 3 | LR2 | 汚染物質含有材料の使用回避 | 0.2
3.1 | Use of Materials without Harmful Substances | 0.3 | 0 | 0.3 | 0 |  |  | 1 | 0 | 0.3 | 0 | 3.1 | LR2 3 | Use of Materials without Harmful Substances | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 3.1 | LR2 3 | 有害物質を含まない材料の使用 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 3.1 | LR2 3 | 有害物質を含まない材料の使用 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 3.1 | LR2 3 | Use of Materials without Harmful Substances | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | 3.1 | LR2 3 | 有害物質を含まない材料の使用 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 3.1 | LR2 3 | 有害物質を含まない材料の使用 | 0.6
3.2 | Avoidance of CFCs and Halons | 0.7 | 0 | 0.7 | 0 | 1 | 0 | 1 | 0 | 0.7 | 0 | 3.2 | LR2 3 | Avoidance of CFCs and Halons | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 3.2 | LR2 3 | フロン・ハロンの回避 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 3.2 | LR2 3 | フロン・ハロンの回避 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 |  |  |  | 3.2 | LR2 3 | Avoidance of CFCs and Halons | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 |  |  |  |  | 3.2 | LR2 3 | フロン・ハロンの回避 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 3.2 | LR2 3 | フロン・ハロンの回避 | 0.4
3.2.1 | Fire Retardant | 0.33333 | 0 | 0.33333 | 0 |  |  | 1 | 0 | 0.33333 | 0 | 3.2.1 | LR2 3.2 | Fire Retardant | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.2.1 | LR2 3.2 | 消火剤 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.2.1 | LR2 3.2 | 消火剤 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3.2.1 | LR2 3.2 | Fire Retardant | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  |  | 3.2.1 | LR2 3.2 | 消火剤 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.2.1 | LR2 3.2 | 消火剤 | 0
3.2.2 | Foaming Agents (Insulation Materials, etc.) | 0.33333 | 0 | 0.33333 | 0 |  |  | 1 | 0 | 0.33333 | 0 | 3.2.2 | LR2 3.2 | Foaming Agents (Insulation Materials, etc.) | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.2.2 | LR2 3.2 | 発泡剤（断熱材等） | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.2.2 | LR2 3.2 | 発泡剤（断熱材等） | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3.2.2 | LR2 3.2 | Foaming Agents (Insulation Materials, etc.) | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  |  | 3.2.2 | LR2 3.2 | 発泡剤（断熱材等） | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.2.2 | LR2 3.2 | 発泡剤（断熱材等） | 0
3.2.3 | Refrigerants | 0.33333 | 0 | 0.33333 | 0 |  |  | 1 | 0 | 0.33333 | 0 | 3.2.3 | LR2 3.2 | Refrigerants | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.2.3 | LR2 3.2 | 冷媒 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.2.3 | LR2 3.2 | 冷媒 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3.2.3 | LR2 3.2 | Refrigerants | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  |  | 3.2.3 | LR2 3.2 | 冷媒 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.2.3 | LR2 3.2 | 冷媒 | 1
LR3 | Off-site Environment | #VALUE! | 0 | #VALUE! | 0 | #VALUE! | 0 | #VALUE! |  | 0.3 | 0 | LR3 | LR | Off-site Environment | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | LR3 | LR | 敷地外環境 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | LR3 | LR | 敷地外環境 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | LR3 | LR | Off-site Environment | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | LR3 | LR | 敷地外環境 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | LR3 | LR | 敷地外環境 | 0.1
1 | Consideration of Global Warming | #VALUE! | 0 | #VALUE! | 0 |  |  | #VALUE! | 0 | 0.33333 | 0 | 1 | LR3 | Consideration of Global Warming | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 1 | LR3 | 地球温暖化への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 1 | LR3 | 地球温暖化への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 1 | LR3 | Consideration of Global Warming | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  |  | 1 | LR3 | 地球温暖化への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 1 | LR3 | 地球温暖化への配慮 | 0
2 | Consideration of Local Environment | #VALUE! | 0 | 0.33333 | 0 | 1 | 0 | 1 | 0 | 0.33333 | 0 | 2 | LR3 | Consideration of Local Environment | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 2 | LR3 | 地域環境への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 2 | LR3 | 地域環境への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 2 | LR3 | Consideration of Local Environment | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  |  | 2 | LR3 | 地域環境への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 2 | LR3 | 地域環境への配慮 | 1
2.1 | Air Pollution | 0.25 | 0 | 0.25 | 0 |  |  | 1 | 0 | 0.25 | 0 | 2.1 | LR3 2 | Air Pollution | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.1 | LR3 2 | 大気汚染防止 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.1 | LR3 2 | 大気汚染防止 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.1 | LR3 2 | Air Pollution | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  |  | 2.1 | LR3 2 | 大気汚染防止 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.1 | LR3 2 |  | 0
2.2 | Heat Island Effect | 0.5 | 0 | 0.5 | 0 |  |  | 1 | 0 | 0.5 | 0 | 2.2 | LR3 2 | Heat Island Effect | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 2.2 | LR3 2 | 温熱環境悪化の改善 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 2.2 | LR3 2 | 温熱環境悪化の改善 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 2.2 | LR3 2 | Heat Island Effect | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | 2.2 | LR3 2 | 温熱環境悪化の改善 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 2.2 | LR3 2 |  | 0
2.3 | Load on Local Infrastructure | 0.25 | 0 | 0.25 | 0 | 1 | 0 | 1 | 0 | 0.25 | 0 | 2.3 | LR3 2 | Load on Local Infrastructure | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.3 | LR3 2 | 地域インフラへの負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3 | LR3 2 | 地域インフラへの負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3 | LR3 2 | Load on Local Infrastructure | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  |  | 2.3 | LR3 2 | 地域インフラへの負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.3 | LR3 2 |  | 0
2.3.1 | Reduction of Rainwater Discharge Loads | 0.25 | 0 | 0.25 | 0 |  |  | 1 | 0 | 0.25 | 0 | 2.3.1 | LR3 2.3 | Reduction of Rainwater Discharge Loads | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.3.1 | LR3 2.3 | 雨水排水負荷低減 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3.1 | LR3 2.3 | 雨水排水負荷低減 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3.1 | LR3 2.3 | Reduction of Rainwater Discharge Loads | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  |  | 2.3.1 | LR3 2.3 | 雨水排水負荷低減 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.3.1 | LR3 2.3 |  | 0
2.3.2 | Sewage Load Suppression | 0.25 | 0 | 0.25 | 0 |  |  | 1 | 0 | 0.25 | 0 | 2.3.2 | LR3 2.3 | Sewage Load Suppression | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.3.2 | LR3 2.3 | 汚水処理負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3.2 | LR3 2.3 | 汚水処理負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3.2 | LR3 2.3 | Sewage Load Suppression | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  |  | 2.3.2 | LR3 2.3 | 汚水処理負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.3.2 | LR3 2.3 |  | 0
2.3.3 | Traffic Load Control | 0.25 | 0 | 0.25 | 0 |  |  | 1 | 0 | 0.25 | 0 | 2.3.3 | LR3 2.3 | Traffic Load Control | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.3.3 | LR3 2.3 | 交通負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3.3 | LR3 2.3 | 交通負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3.3 | LR3 2.3 | Traffic Load Control | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  |  | 2.3.3 | LR3 2.3 | 交通負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.3.3 | LR3 2.3 |  | 0
2.3.4 | Reduction of Waste Treatment Loads | 0.25 | 0 | 0.25 | 0 |  |  | 1 | 0 | 0.25 | 0 | 2.3.4 | LR3 2.3 | Reduction of Waste Treatment Loads | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.3.4 | LR3 2.3 | 廃棄物処理負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3.4 | LR3 2.3 | 廃棄物処理負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  | 2.3.4 | LR3 2.3 | Reduction of Waste Treatment Loads | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 |  |  |  |  | 2.3.4 | LR3 2.3 | 廃棄物処理負荷抑制 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 2.3.4 | LR3 2.3 |  | 0
0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [65 empty] | 2.3.4 | LR3 2.3 | 廃棄物処理負荷抑制 | 1
3 | Consideration of Surrounding Environment | #VALUE! | 0 | 0.33333 | 0 | 1 | 0 | 1 | 0 | 0.33333 | 0 | 3 | LR3 | Consideration of Surrounding Environment | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3 | LR3 | 周辺環境への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3 | LR3 | 周辺環境への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3 | LR3 | Consideration of Surrounding Environment | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  |  | 3 | LR3 | 周辺環境への配慮 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3 | LR3 | 周辺環境への配慮 | 0
3.1 | Noise, Vibration & Odor | 0.4 | 0 | 0.4 | 0 | 1 | 0 | 1 | 0 | 0.4 | 0 | 3.1 | LR3 3 | Noise, Vibration & Odor | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 3.1 | LR3 3 | 騒音・振動・悪臭の防止 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | 3.1 | LR3 3 | 騒音・振動・悪臭の防止 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | 3.1 | LR3 3 | Noise, Vibration & Odor | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  |  | 3.1 | LR3 3 | 騒音・振動・悪臭の防止 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 3.1 | LR3 3 |  | 0
3.1.1 | Noise | 0.33333 | 0 | 0.33333 | 0 |  |  | 1 | 0 | 0.33333 | 0 | 3.1.1 | LR3 3.1 | Noise | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.1.1 | LR3 3.1 | 騒音 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3.1.1 | LR3 3.1 | 騒音 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3.1.1 | LR3 3.1 | Noise | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  |  | 3.1.1 | LR3 3.1 | 騒音 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.1.1 | LR3 3.1 |  | 0
3.1.2 | Vibration | 0.33333 | 0 | 0.33333 | 0 |  |  | 1 | 0 | 0.33333 | 0 | 3.1.2 | LR3 3.1 | Vibration | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.1.2 | LR3 3.1 | 振動 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3.1.2 | LR3 3.1 | 振動 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3.1.2 | LR3 3.1 | Vibration | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  |  | 3.1.2 | LR3 3.1 | 振動 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.1.2 | LR3 3.1 |  | 0
3.1.3 | Odor | 0.33333 | 0 | 0.33333 | 0 |  |  | 1 | 0 | 0.33333 | 0 | 3.1.3 | LR3 3.1 | Odor | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.1.3 | LR3 3.1 | 悪臭 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3.1.3 | LR3 3.1 | 悪臭 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  | 3.1.3 | LR3 3.1 | Odor | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 |  |  |  |  | 3.1.3 | LR3 3.1 | 悪臭 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0 | 0 | 0 | 3.1.3 | LR3 3.1 |  | 0
3.2 | Wind/Sand Damage & Sunlight Obstruction | 0.4 | 0 | 0.4 | 0 | 1 | 0 | 1 | 0 | 0.4 | 0 | 3.2 | LR3 3 | Wind/Sand Damage & Sunlight Obstruction | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 3.2 | LR3 3 | 風害、日照阻害の抑制 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | 3.2 | LR3 3 | 風害・砂塵、日照阻害の抑制 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | 3.2 | LR3 3 | Wind/Sand Damage & Sunlight Obstruction | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  |  | 3.2 | LR3 3 | 風害・砂塵、日照阻害の抑制 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 3.2 | LR3 3 |  | 0
3.2.1 | Restriction of Wind Damage | 0.7 | 0 | 0.7 | 0 |  |  | 1 | 0 | 0.7 | 0 | 3.2.1 | LR3 3.2 | Restriction of Wind Damage | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0 | 0 | 0 | 3.2.1 | LR3 3.2 | 風害の抑制 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 |  |  |  | 3.2.1 | LR3 3.2 | 風害の抑制 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 |  |  |  | 3.2.1 | LR3 3.2 | Restriction of Wind Damage | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 |  |  |  |  | 3.2.1 | LR3 3.2 | 風害の抑制 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0 | 0 | 0 | 3.2.1 | LR3 3.2 |  | 0
3.2.2 | Control of Sand and Dust | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 0 | 3.2.2 | LR3 3.2 | Control of Sand and Dust | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2.3 | LR3 3.3 | 砂塵の抑制 | [9 empty] | 0.2 |  |  |  | 3.2.2 | LR3 3.2 | 砂塵の抑制 | [9 empty] | 0.2 |  |  |  | 3.2.2 | LR3 3.2 | Control of Sand and Dust | [9 empty] | 0.2 |  |  |  |  | 3.2.2 | LR3 3.2 | 砂塵の抑制 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2.2 | LR3 3.2 |  | 0
3.2.3 | Restriction of Sunlight Obstruction | 0.3 | 0 | 0.3 | 0 |  |  | 1 | 0 | 0.3 | 0 | 3.2.3 | LR3 3.2 | Restriction of Sunlight Obstruction | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0 | 0 | 0 | 3.2.2 | LR3 3.2 | 日照阻害の抑制 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 |  |  |  | 3.2.3 | LR3 3.2 | 日照阻害の抑制 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 |  |  |  | 3.2.3 | LR3 3.2 | Restriction of Sunlight Obstruction | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 |  |  |  |  | 3.2.3 | LR3 3.2 | 日照阻害の抑制 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0 | 0 | 0 | 3.2.3 | LR3 3.2 |  | 0
3.3 | Light Pollution | 0.2 | 0 | 0.2 | 0 | 1 | 0 | 1 | 0 | 0.2 | 0 | 3.3 | LR3 3 | Light Pollution | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 3.3 | LR3 3 | 光害の抑制 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3 | LR3 3 | 光害の抑制 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | 3.3 | LR3 3 | Light Pollution | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | 3.3 | LR3 3 | 光害の抑制 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 3.3 | LR3 3 |  | 0
3.3.1 | Outdoor Illumination and Light that Spills from Interiors | 0.7 | 0 | 0.7 | 0 |  |  | 1 | 0 | 0.7 | 0 | 3.3.1 | LR3 3.3 | Outdoor Illumination and Light that Spills from Interiors | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 3.3.1 | LR3 3.3 | 屋外照明及び屋内照明のうち外に漏れる光への対策 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 |  |  |  | 3.3.1 | LR3 3.3 | 屋外照明及び屋内照明のうち外に漏れる光への対策 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 |  |  |  | 3.3.1 | LR3 3.3 | Outdoor Illumination and Light that Spills from Interiors | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 |  |  |  |  | 3.3.1 | LR3 3.3 | 屋外照明及び屋内照明のうち外に漏れる光への対策 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 3.3.1 | LR3 3.3 |  | 0
3.3.2 | Measures for Reflected Solar Glare from Building Walls | 0.3 | 0 | 0.3 | 0 |  |  | 1 | 0 | 0.3 | 0 | 3.3.2 | LR3 3.3 | Measures for Reflected Solar Glare from Building Walls | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 3.3.2 | LR3 3.3 | 昼光の建物外壁による反射光（グレア）への対策 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 3.3.2 | LR3 3.3 | 昼光の建物外壁による反射光（グレア）への対策 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  | 3.3.2 | LR3 3.3 | Measures for Reflected Solar Glare from Building Walls | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 |  |  |  |  | 3.3.2 | LR3 3.3 | 昼光の建物外壁による反射光（グレア）への対策 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 3.3.2 | LR3 3.3 |  | 0

## Credit
Comprehensive Assessment System for Built Environment Efficiency
CASBEE for Building Design (New Construction) 2024 Edition
Assessment Software
Microsoft Excel 2019
CASBEE-BD_NCe_2024v1.21
Published in 2025
Software development: Japan Sustainable Building Consortium (JSBC)
(Research Committee on Comprehensive Assessment System for Built Environment Efficiency)
Inquiries concerning software content, etc. :
Inquiries concerning the content of this software should be sent by e-mail only to the address below. A few days may be required before you receive a reply. Please refer to the manuals for Microsoft Windows, Microsoft Excel 2019, and other software for instructions on their use.
Institute for Built Environment and Carbon Neutral for SDGs(IBECs)
HB Hirakawacho bldg. 2-8-9. Hirakawacho, Chiyoda-ku,Tokyo,102-0093 Japan
E-Mail casbee-info@ibecs.or.jp
URL https://www.jsbc.or.jp/research-study/casbee.html
Copyright ©2025 Japan Sustainable Building Consortium（JSBC）
Important Notes (Conditions of Use)
1) Microsoft Excel 2019 is a registered trademark of Microsoft Corporation in the United States of America and other countries.
2) Other company names and product names are trademarks or registered trademarks of the companies concerned.
3) CASBEE for Building Design (New Construction) consists of data files that were developed using Microsoft Excel 2019. These data files are protected by copyright law. They may not be duplicated or transferred (even in modified form) without the consent of the developers, authors, planners, and publishers.
4) This restriction does not apply to the use of input data and output results prepared on this software by its users. In such cases, the data concerned should include a statement to the effect that it was prepared using this assessment software. Note that the additional consent of Microsoft Corporation may be required for the use of screen images.
5) We accept no liability for the results of using this software or its instruction manual.
6) The specifications of this software and the contents of the operation manual are subject to change without prior notice.
7) This software was created using Microsoft Excel 2019. We do not guarantee its operation on all computers.